PfS Contractors Framework

Invitation to Tender Volume 5

Part 2 Facilities Output Specification

Design Brief

Part B1-Generic

Buildings and Grounds Requirements

January 2010

Document Control

PfS and its advisers accept no liability whatsoever for any expense, liability, loss, claim or proceedings arising from reliance placed upon this Template Document for the Invitation to Tender

| Document Properties |  |
| --- | --- |
| Document Owner | Academies Director |
| Organisation | Partnerships for Schools |
| Title | PfS Contractors’ Framework Template Document Invitation to Tender – Volume 5 Part 2 – Facilities Output Specification, Design Brief Part B1- Generic Buildings and Grounds Requirements |
| Abstract |  |
| This ITT template should be read in conjunction with the following guidance and template documents: - Invitation to Tender for Local Competition Volumes 1-8 - Local Competition Guidance |  |

| Version History |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date | Editor | Version | Status | Reason for change |
| 25/10/2010 | JS | 1.0 | Issued | First issue for PfS Contractors Framework |

Contents

Section 1: Design Principles

1.1 Site Plan and Location

Site Layout and Landscaping

1.2 Access and Inclusion

Wayfinding

Inclusion

1.3 Organisation and Layout

typical organisation

schedule of accommodation

links and adjacencies

1.4 Internal Space

Critical Design Criteria

Dimensions and proportions

General learning spaces

Light Practical learning spaces

Science

Design and Technology

Heavy Practical learning spaces

Large and Performance learning spaces

Music

Indoor PE and Sport

Main Hall

Entrances

Administration areas

Central Storage

Catering Facilities

Dining spaces

Kitchen facilities

Learning Resources and Inclusion Facilities

Library resource centre

Small group rooms

Medical, therapy and other support

Multi-agency provision

Supplementary areas

Toilets

1.5 External Space: Grounds

Typical organisation

Protection of School Playing Fields

All Weather Pitches

Informal and Social Areas

Hard Surfaced Games Courts

Multi-use Games Areas (MUGAs)

Sports Pitches

Pitch Layouts and orientation

Access Areas

Paths, Roads and Delivery Areas

Drop-off [and bus turnaround] provision

Parking and cycle storage

Section 2: Design Outcomes

2.1 Flexibility and Adaptability

Flexibility

Adaptability

Expandability

- 2.2 Enhancing learning

2.3 Enhancing schools’ ethos

- 2.4 Identity and Community context

- 2.5 Welcoming and Secure

- Controlled access

### Security Technology and Alarms

Fencing

Section 3 – Environmental Conditions

3.1 Internal Environment

Acoustics

Daylight

Glare

### Temperature

Solar Gain

Thermal Performance

Ventilation

Specialist ventilation

Environmental controls

3.2 Building Services

Heating systems

Heating Controls

Water

Drainage installations

Gas and compressed air installations

Fire fighting installation

Sprinklers

Building Management System

Internal Lighting [systems]

Efficacy

Adaptability

Lighting Controls

Emergency Lighting

External and Specialist Lighting

Mains distribution

Power circuits

Clock installation

Lightning protection

Lift installation

Protective systems

Intruder alarms

CCTV

Communication Systems

Fire alarm system

Period bell and PA system

ICT Infrastructure (data cabling and telecommunications)

TV installation

3.3 Form and structure

Substructure

3.4 Building fabric and materials

General

Use of Materials

Building Fabric

Roofs

Chimneys and flues

Rainwater goods

Stairs, ramps and handrails

External walls

External doors and windows

Internal Walls Internal doors

Ironmongery

Floor finishes

Ceilings

### Internal Decorations and Finishes

3.5 Details and integration

Sanitary fittings

Signage

Integrations with ICT and F&E

3.6 Sustainable Design

Developing an Environmental Assessment

### Water Conservation

### Low Carbon

Lighting Efficiency

Efficient Equipment

Climate Change Adaptation

### Material Efficiency Reducing Waste during Construction

### Requirement for higher recycled content

### Timber

Section 4 – Facilities Management and Construction

4.1 Operability

4.2 Design life and maintenance

Planned Maintenance Programme

Maintenance Access

Finishes

4.3 Compliance with Standards and Guidelines

4.4 Phasing and Construction

Summary of Design Objectives

The Minimum Design Standard for BSF, jointly developed by the Department for Children Schools and Families (DCSF), Partnerships for Schools (PfS) and the Commission for Architecture and the Built Environment (CABE), will mean that designs which do not meet the rigorous standard will not be able to proceed through procurement.

This Design Brief covers the objectives and requirements for the design of the buildings and grounds of any school. This Part B1 specifies the generic requirements for all schools or Academies designed and constructed within the framework. Part B2 specifies the school-specific requirements for each school.

The Contractors proposals shall comply with the overarching design objectives set out in the CABE review ten points for good design, which are identified at the start of each of the following 20 sub-sections in this Design Brief. The table below shows how the CABE ten points link to the sub-headings in Sections 1 to 4, as well as the key statements in the DQI for Schools:

| Design Brief sub-sections | CABE 10 points | DQI for Schools statements |
| --- | --- | --- |
| Section 1: Design Principles |  | Functionality |
| 1.1 Site Plan and Location | 2. site plan: making the best use of the site | Access: It should be easy to find your around the school |
| 1.2 Access and Inclusion | 4. Organisation: creating a clear diagram for the buildings | Access: The building should provide good access to everyone |
| 1.3 Organisation and Layout |  | - |
| 1.4 Internal Space | 6. Interiors: creating excellent spaces for learning and teaching | Space: the spaces should be right size for their functions |
| 1.5 External Space | 3. School grounds: making assets of the outdoor spaces | Space: the grounds should provide for the formal and informal teaching and learning, and social and recreational, needs of the school and community |
| Section 2: Design Outcomes |  |  |
| 2.1 Flexibility and Adaptability | 9. Long life, loose fit: creating a school that can adapt and evolve in the future | Uses: the building and grounds should be able to respond to changing school needs |
| 2.2 Enhancing Learning | 10. successful whole: making a design that works in the round | Uses: the building should enhance the activities of teaching and learning |
|  |  | Impact |
| 2.3 Enhancing Ethos | 1. Identity and context: making a school the students and community can be proud of | Character and Innovation: the building and grounds should lift the spirits and raise aspirations |
| 2.4 Identity and community Use |  | The school in the community: the building should enhance and uplift its neighbourhood |
| 2.5 Welcoming and Secure | 8. feeling safe: creating a secure and welcoming place | Within the School: the building should be a pleasure to use |
| Section 3: Environmental Conditions |  |  |
| 3.1 Internal Environment | 6. Interiors: creating excellent spaces for learning and teaching 7. Resources: deploying convincing environmental strategies | Within the School: the internal environment should be of high quality with an appropriate level of personal control |
| 3.2 Building Services |  |  |
| 3.3 Form and Structure | 5. Buildings: making form, massing and appearance work together | Form and Materials: the building should be well composed |
| 3.4 Building fabric and materials |  |  |
|  |  | Build Quality |
| 3.5 Details and Integration |  | Construction: the construction should be well thought through |
| 3.6 Sustainable Design | 7. Resources: deploying convincing environmental strategies | Construction: the design will be sustainable-environmentally conscious |
|  |  | Engineering Services: the building should enable efficient use of energy and water |
| Section 4: Facilities Management and Construction |  |  |
| 4.1 Operability | [usability issues from 6 above] |  |
| 4.2 Design life and maintenance | [durability issues from 5 above] | Performance: the building should be easily maintained |
| 4.3 Compliance | - | Performance: the environment should meet recommended standards |
| 4.4 Construction/ phasing | - | - |

Section 1: Design Principles

This section identifies the strategic, overarching design principles for access, organisation and space, both internal and external, It considers these requirements from ‘the outside in’ – from location, through access and organisation of space to more specific requirements for various areas of the buildings and grounds.

## Site Plan and Location

    - The design should make good use of the site, balancing the needs of pedestrians, cyclists and cars and enhancing the school’s presence in the community. It should maximise the potential use of every site and thoughtfully locate any new buildings, in a manner that will permit possible future extensions.

    - All designs shall address the following points, as listed in the CABE review requirements for site plan: making the best use of the site:

- The design should foster a sense of place

- The design should deal with site-specific constraints well

- The buildings, grounds and facilities should be arranged well on the site

- The configuration of buildings should create positive internal an external spaces

- The external circulation routes should be clear and balance the demands of different users

### Site Layout and Landscaping

    - The landscape and layout should show appropriate and safe vehicular and pedestrian access circulation both within the site (including between use zones) and within the local context. Such provision should include access to and through soft landscape areas, (for example, to habitat zones or sensory gardens) along defined and protected pathways that do not require special footwear and are easily maintained.

    - The design of the site layout shall:

- take account of the character of the area, the topography of the site, including its shape, contours and subsoil, and its exposure to wind and rain;

- exploit views and mitigate the effects of adverse environmental conditions such as traffic noise, unattractive views, or neighbours in close proximity, including any highlighted in Part B2;

- allow for supervision, where possible over more than one activity at a time;

- provide a secure environment which discourages trespass and vandalism;

- provide easy access between changing rooms and outdoor PE facilities, and between community parking areas and parts of the buildings and grounds likely to be used outside school hours;

- ensure all external areas, including roads, paths, ramps and entrances, are fully negotiable by disabled users;

- locate facilities, activities and circulation safely;

- provide safe and convenient access for pedestrians and cyclists, with safe access and secure storage for goods and waste;

- provide sufficient car parking, as well as separate bays for disabled users and visitors, in line with the number of bays required in Part B2;

- provide good access to public transport where it is available.

    - Main and secondary site entrances shall incorporate some form of controlled access and allow manual supervision with clear sight lines in order to manage the movement of pupils and visitors on the school site.

    - The Contractor shall ensure that any all-weather surfaces provided should be located such that users do not have to cross grass to reach them, as this will prevent wheelchair users from accessing them and is likely to result in mud being trodden into the surface.

## Access and Inclusion

    - It should be easy to find your way around the school and there should be clarity in the arrangement and location of entrances, main circulation routes and key spaces. The buildings and grounds should provide good access for everyone in line with national and local inclusion policies.

    - All designs shall address the following points, as listed in the CABE review requirements for organisation: creating a clear diagram for the building :

- there should be a clear hierarchy of circulation routes

- Links between indoor and outdoor spaces should be optimised

### Wayfinding

    - The building layout shall be clearly organised to enable ease of circulation for pupils, visitors and teachers. This must be achieved at an early design stage and utilise the building architecture as well as just signage. However, appropriate signage or way finding shall be provided where necessary to enable new visitors to understand the layout of the school (see signage 3.5).

    - The layout of spaces within the school shall be simple with a clearly defined layout to aid orientation. Especially important is ease of movement to external areas, particularly at times of emergency and for those with restricted mobility.

    - There must be one easily supervised and clearly identified entry point to the buildings for visitors to the schools with signage directing visitors from the entry of the site to the Visitor’s Reception (see entrances). Entry/exit points for pupils must be strictly controlled either within the building or within the overall site.

### Inclusion

    - All new buildings, and as far as possible refurbished schools, should seek to promote equal opportunities by being fully accessible to all people including those with impaired movement or other disabilities, including impaired sight and impaired hearing. This applies to students and staff as well as visitors and other members of the wider community. People with disabilities should not be placed at a disadvantage by the design of the building and should be able to use the same entrances and access routes as able bodied users. The design of access points and circulation routes should assist people with impairments such as mobility, sight or hearing.

    - All designs shall satisfy all relevant and current legislation and best practice guidance, as listed in Annex [1 and 2], such that each design proposal will provide the following design features:

- Circulation, both internal and external that is accessible for people with disabilities and special needs.  This will include readily identifiable routes (‘way finding’ schemes) with colour contrast, tactile surfaces and good quality lighting and decoration to include good visual contrast and clarity of changes in levels and surfaces

- Space for wheelchairs available in corridors, as well as space for other appliances to be ‘parked’ or stored off circulation areas

- Signage of appropriate size lettering with visual contrast to the background installed at an appropriate height where it is clearly visible to users, with tactile signage provided where requested in Part B2 of this Design Brief

- Doors that are easy to identify and operate and allow wheelchair accessibility to all relevant spaces, with space for approach and operation of doors. Any single door leaf shall be wide enough to allow access, with good visibility maintained on both sides of the door.  Double doors within corridors may be held open on electromagnetic catches linked to the fire detection system. Ramps and stairs that have the shallow gradients and pitch required by the DCSF Constructional Standards with suitable handrails, balustrades and guardings which are attractive and easy to use by everyone.

- Lifts that are sufficiently large and user friendly capable of restriction on user types.

- Lighting and blinds appropriate to provide suitable light and to avoid glare for those with visual impairments. Downlighting should be avoided at reception and in teaching spaces, where cast shadows make lip reading difficult.

- Finishes that use appropriate materials such that ceilings and walls have good light reflectance and acoustic absorption, floors allow for safe ease of movement, with suitable slip resistance and acoustic absorption, and acoustically hard surfaces which create unwanted background noise are avoided where possible.

## Organisation and Layout

    - The design should provide a good organisation of spaces in plan and section, easily legible and fully accessible, with circulation that is well organised and imaginatively designed, and good arrival space to suit the community as well as the school.

    - All designs shall address the following points as listed in the CABE review requirements for organisation: creating a clear diagram for the buildings:

- The educational agenda should be successfully accommodated in the internal arrangement of spaces

- There should be a clear spatial diagram for the building

- The learning spaces should be arranged well across the school

- 

### Typical Organisation

    - All schools will comprise various suites of flexible learning spaces and associated ancillary accommodation: These suites of spaces shall be designed such that they can accommodate the model(s) of organisation and pedagogy that the school are proposing in the Educational Brief, as well as allowing other models in the future.

### Schedule of Accommodation

    - The Contractor shall provide a schedule of ‘as designed’ accommodation that compares the spaces proposed to those required in the Schedule of Accommodation for each school, in a format that allows easy comparison of individual areas, the total area of each category of space and the net capacity achieved.

### Links and Adjacencies

    - Area relationships and adjacencies, of both spaces and suites of spaces, must be as required by the Framework User in Part B2 of this Design Brief.

## Internal Space

    - Learning spaces should be the right size for their functions, well proportioned, fit for purpose and meet the needs of the curriculum. There should be sufficient teaching and learning spaces to provide the number of pupils places planned (as measured by the net capacity assessment method), as specified in the Schedule of Accommodation [at Annex 3].

    - All designs shall address the following points as listed in the CABE review requirements for interiors: creating excellent spaces for learning and teaching:

- Occupants should experience variety and delight as they move around the school

- Circulation and social areas should be inviting to students

- The internal environment should help students and staff feel valued and motivated

- Learning spaces should be well proportioned and pleasant

### Critical Design Criteria

    - Basic teaching spaces or learning areas, as discussed below and identified specifically in Area Data Sheets, shall be:

- accommodated within adaptable zones to allow a number of rooms of differing sizes and types;

- designed such that they can be linked with internal doors and windows, semi-open or even defined by furniture and screens in some cases;

- designed to be within an adaptable area which allows a number of spaces, including circulation routes where appropriate, to be used in a wide variety of ways in the future (see ‘adaptability’ at 2.1).

### Dimensions and Proportions

    - The preferred area and minimum dimensions for each space are specified in the Area Data Sheets.

### General Learning Spaces

    - General teaching spaces will be able to accommodate a range of general teaching activities and subjects as well as providing a registration, and perhaps social, base for a year- or mixed-age group. While they are not usually expected to be serviced with more than power and ICT infrastructure, the opportunity to add serviced facilities to enable some light practical activities in some rooms would be beneficial.

    - The Contactor shall be aware of the best-practice recommended in BB92 Modern Foreign Languages: a Design Guide and BB99: A Briefing Guide for Primary Schools, and be able to demonstrate that this is inherent in all general teaching areas where relevant.

### Light Practical Learning Spaces

    - Light practical teaching spaces will provide a larger area for each workplace and will be serviced, at least with water, as identified in the Area Data Sheets. However, any services  should be fitted with sufficient master controls and each space should be flexible enough to be usable for non-practical activities such as providing a registration base.

### Science

    - In line with the recent work done for the DCSF in the Faraday Project the options for learning spaces for science in mainstream secondary schools are far wider than simply general laboratories. Even where schools currently prefer a more traditional arrangement of multi-purpose laboratories, therefore, the Contractor should be able to demonstrate the future opportunities of a wider range of science accommodation within the same building envelope.

    - The Contractor shall ensure that, where required, separate, lockable storage is provided for:

- Explosive and other dangerous material, including gas cylinders and radioactive samples;

- Chemicals and other hazardous materials in use in specific teaching areas as identified on Area Data Sheets.

    - In addition to the above, Contractors should be able to show how their proposals are in line with best practice set out for science accommodation in Project Faraday: Exemplar designs for science, the second edition of BB80 Science Accommodation in Secondary Schools and other relevant documents as listed by the Association for Science Education (ASE). In particular:

- Sufficient and appropriately positioned central preparation rooms, with easy access to a deliveries point and teaching spaces, but not limiting adaptability between laboratories;

- .

### Art

    - As well as responding to the specific requirements in the Part B2 of this Design Brief and the Area Data Sheets for art in each school, the Contactor shall be aware of the guidance in BB89 Art Accommodation in Secondary Schools and the SSAT publication Arts spaces in schools: designing for excellence [ref], and should be able to show that their proposals are in line with the best practice identified in these documents. In particular, rooms used for art should have:

- good daylight (typically from the North), views (for instance from upper floors) and links to outdoor areas where possible;

- opportunities for both horizontal and vertical display of two- and three-dimensional work;

- sufficient walk-in storage for both resources and work-in-progress accessible from each art room.

### Design and Technology

    - As well as responding to the specific requirements in the Part B2 of this Design Brief and the Area Data Sheets for indoor design and technology spaces in each school, the Contractor shall be aware of the any design guidance available from the Design and Technology Association (DATA). Where Design and Technology spaces are specified, the Contractor shall be able to demonstrate how their proposals meet the criteria set out in BB81 Design Technology in Secondary Schools. In particular:

- the adjacencies and proportions of teaching spaces such as workshops, to allow flexibility in the range of possible layouts and uses;

- the proportions and accessibility of the preparation area for resistant materials, such that materials can be delivered, stored and cut to size.

### Heavy Practical Learning Spaces

    - Some learning spaces in secondary schools will be heavy practical, fitted with fixed, serviced equipment such as lathes or cookers as identified in the Area Data Sheets. They are not likely to be usable as registration bases, and may be less flexible than other learning areas. They will typically include Design and Technology workshops, food rooms and specialist spaces for engineering or construction where specified in the Schedule of Accommodation.

### Large and Performance Learning Spaces

    - Large and performance teaching spaces will have specific features of volume and/or acoustics as identified in the Area Data Sheets. The Contractor shall ensure that, even where they are linked via sliding/folding walls or doors, the acoustic separation between these spaces is as required in the Area Data Sheets and BB93.

    - It should also be noted that the acoustic requirements identified in the Area Data Sheets for other spaces are based on the assumption that music and drama spaces in mainstream secondary schools will only be accommodated in a suite of performance spaces and associated facilities.

### Music

    - As well as responding to the specific requirements in the Part B2 of this Design Brief and the Area Data Sheets for music, media and drama spaces in each school, the Contactor shall be aware of the guidance in BB86 Music Accommodation in Secondary Schools. Where spaces for music are specified, the Contractor should be able to show that their proposals are in line with the best practice identified in this document. In particular:

- music rooms with acoustic properties matching the requirements of the Area Data Sheets, including the reduction of standing waves from parallel walls;

- group/ practice rooms that are easily accessed and supervised from the main music rooms while being acoustically discrete.

### Indoor PE and Sport

    - The sports facilities shall generally be available to the local community outside the core school day, along with other key areas of the school such as the main hall. The Contractor should therefore be able to demonstrate how these facilities can be used at these times, and accessed safely and easily by the community. They should also be able to show how the opportunities for community use are enhanced by the location of any specific community facilities identified in the Schedule of Accommodation, such as storage, lockers and community office, as well as the design of the entrance and foyer space of this suite of spaces.

    - As well as responding to the specific requirements in the Part B2 of this Design Brief and the Area Data Sheets for indoor PE and sport spaces in each school, the Contactor shall be aware of the recommendations in the Sport England design documents listed in the PfS BSF design guidance: PE & Sport, and the DCSF guidance document Inspirational Guide to PE Spaces, and should be able to show that the design of indoor sport and PE facilities are in line with this guidance. In particular:

- Storage adjacent to sports hall, if specified, on the long side and easily accessible for storage of large items of equipment;

- Separate storage for community-related items and for rubberised matting, with direct ventilation to external air where materials are stored which may give off toxic gases during fire conditions.

### Main Hall

    - Where specified in the Schedule of Accommodation, the main hall and other large spaces are required for assemblies, religious worship and examinations, as well as presentations and activities for large groups, such as projects for a year group. It will also be used for various activities for the community and others outside the school day, such as performances and parent evening events. The contractor should be able to demonstrate how the location and adjacencies of the main hall, foyer and ancillary spaces allow this range of use. In particular, they should enhance the use of the space as a performance space, using ancillary areas for ‘front-of-house’ and ‘back-stage’ activities and allowing the space to be easily accessible from the main entrance.

### Entrance and Administration

    - These areas shall be centrally located yet close to the front of the school, to provide the main entrance and the accommodation that needs to be adjacent to it, including reception, and main office.

### Entrances

    - A clearly defined, accessible and welcoming main entrance should compliment the functions of the school, during and outside of the school day, and out of core teaching times. The image of the school should be hospitable to the whole community in order to encourage a sense of ownership, and accessibility.

    - The entrance shall be designed to provide for disabled users, including those in wheelchairs, and parents with pushchairs and prams to be welcomed and to move comfortably and freely at peak times.

    - Separate access shall be provided for deliveries, maintenance vehicles and personnel and waste removal.

### Administration area

    - The reception area should be adjacent to the main visitor’s entrance, and should be able to be used by administrative staff normally working in the main office. Hence, the office should be adjacent to the reception area, as well as being close to other administrative staff offices or work areas, as defined in the Schedule of Accommodation and Part B2.

    - This area shall also offer a potential area for a ‘sick bay’ where pupils who are unwell can rest and wait to be taken home, while being close to administrative staff.

### Central storage

    - The administration area will generally also be home to central and secure stores as defined in the Schedule of Accommodation and Area Data Sheets for each school, for instance for examination papers, which should be lockable and only accessible from staff areas, such as a corridor only used by staff.

    - Separate storage shall be provided for:

- waste materials, including the facility for separation for recycling purposes;

- external equipment, for instance for maintenance;

- secure waste. This could be internal or alternatively, a secure compound built from incombustible materials and located in accordance with relevant legislation’.

### Catering Facilities

    - The area of the main dining space, or spaces, identified in the Schedule of Accommodation for any mainstream secondary school shall generally be sufficient for at least 80% of the school to have lunch in the equivalent of sittings of at least 15 minutes.

### Dining spaces

    - The number of specific dining spaces, whether a single location or dispersed, shall be as identified in Part B2 of the Design Brief. In mainstream secondary schools, the Contractor shall design the main dining area[s] to suit any alternative uses during the school day identified in Part B2 of the Design Brief. In primary and special schools, the dining spaces may be the hall or other areas and the Contractor shall ensure such space accommodates all activities specified appropriately.

    - As well as responding to the specific requirements in the Part B2 of this Design Brief and the Area Data Sheets for dining and social areas in each school, the Contactor shall be aware of the recommendations of the School Food Trust and should be able to show that the design of catering facilities are in line with the DCSF guidance document Schools for the Future. Inspirational Design for Kitchens and Dining Spaces. In particular:

- any dining area[s] should be designed to encourage good social interaction and provide an interesting and enjoyable context for eating;

- sufficient circulation or other space should be provided next to any dining area for queuing space at meal times.

    - The Contractor shall ensure that the design of any area used as a main dining space:

- allows adequate seating capacity with options for different table layouts

- provides sufficient servery points, with adequate room for attractive food presentation and display;

- provides sufficient space for orderly queuing on the approach to the servery, at peak times, without impinging on the dining tables [and preferably in a different space];

- includes a flow diagram to demonstrate the logical flow of children round the dining space from arrival, queuing to collect food, both hot and cold food, eating and self-clearing (such that those clearing empty plates do not conflict with carrying full plates and contra-flows or confusing options are avoided);

- allows for an efficient layout, for fast service, and enough till points (appropriate to the payment system used) to service the number of diners in any sitting;

- considers the acoustic strategy to reduce noise.

### Kitchen Facilities

    - The Contractor shall ensure that the design and location of the school kitchen and associated areas, including office, toilets, changing and staff areas, has involved a specialist consultant and provides:

- a functional layout that allows efficient operations in line with the requirements of the new food standards [ref], arranging the main activity areas of delivery, storage, preparation, cooking and wash up in a logical sequence to ease work flows;

- a sensible ‘flow’ from the self clearing facility linking to the kitchen pre-clean area and dish wash, and from dishwasher to crockery/cutlery/tray storage;

- adequate but secure servicing access for deliveries of ingredients and equipment and disposal, recycling and collection of waste;

- the capability to prevent unauthorised access when required

- minimal impact on the school and educational operation, including noises and smells in adjacent areas;

- durable, hygienic, easily cleanable materials;

- pleasant working conditions, including daylight, views and adequate staff accommodation.

### Learning Resources and Inclusion Facilities

    - While the suites of spaces accommodating the facilities identified above may have some local learning resources, such as a small group room, the central library or learning resources centre will usually be central, along with support spaces for inclusion.

### Library Resource Centre

    - Where specified in the Schedule of Accommodation, the library resource centre should be capable of being a quiet space, with one entrance and exit via a security system unless otherwise specified in the Area Data Sheet. It may be adjacent to sixth form study areas or library space specifically for them.

    - As well as responding to the specific requirements in the Part B2 of this Design Brief and the Area Data Sheets for the [learning resource centre] in each school, the Contractor should be aware of the Libraries Association DVD and associated material [ref] and be able to demonstrate that the library or learning resource centre in each school is designed following the principles and recommendations therein where possible. In particular:

- Where specified, the librarian’s desk should be positioned such that it is adjacent to the entrance but has sightlines to all parts of the library area;

- Mezzanine areas should be avoided unless there is a specific purpose that can be identified that can be utilised without supervision from the main area.

### Small Group Rooms

    - Small group rooms throughout the school, where specified in the Schedule of Accommodation, shall be designed to provide discrete, quiet spaces for learning support, for instance with a foreign language assistant, behaviour management or private counselling.

### Medical, Therapy and Other Support

    - Most schools shall have a room capable of being used by a physiotherapist. In special schools and some specially resourced provision, the Contractor shall provide further specialist facilities as specified in the Schedule of Accommodation and Area Data Sheets. These may include a sensory room, soft play, calming room or hydrotherapy pool and associated changing and plant.

### Multi-agency provision

    - Where specified in the Area data Sheets, some of the support facilities may be jointly used by partner organisations as part of the extended schools agenda, to encourage integrated working for instance with Health, Educational Psychologists, Social Care, AEN Team, Youth Workers, or Connexions. These spaces shall be designed and positioned such that they can be offered to others to use at specific times of the week and outside the schools’ core hours.

### Supplementary Areas

    - Where specified in the Schedule of Accommodation, the Contractor shall provide or refurbish area supplementary to the core school needs, for instance for specially resourced provision for additional places for pupils with specific special needs in a mainstream school, or for additional space related to community use or funded from other sources.

### Toilets

    - The design and construction of all toilets shall comply with the requirements set out in ‘SSLD 3: Toilets in Schools’, such that the minimum standards and dimensions set out in the ‘key performance requirements’ are achieved in all toilets wherever it is reasonable and appropriate.

    - These are as well as the specifications within the Area Data Sheets for toilets, also based on the same document, which attempt to discourage the anti-social behaviour that often occurs when pupils socialise and ‘hang around’ in the toilets.

    - The following requirements will also apply to all toilets:

- The Contractor shall comply with the minimum requirements of the Education (Schools Premises) Regulations 1999 and the Workplace (Health Safety and Welfare) Regulations 1992 with regard to the minimum number of sanitary fittings required on the site.

- Female toilets for pupils over the age of 8 are to be provided with sanitary disposal units.

- All sanitary fittings shall be as specified in section 3.5

- Toilets for pupils must be separate from those for staff except those for disabled pupils which may be used by staff or visitors.

### Circulation

    - There shall be ease of access to central spaces such as the hall, ICT suites and specialist resource rooms from all areas of the school. Primary circulation shall be at least the area allowed in the Schedule of Accommodation.

    - Internal circulation shall comply with the following requirements:

- Suitable and fit for purpose access control mechanisms must be provided externally to all main reception areas.

- The entrance lobbies for the schools and their facilities shall be of adequate size for peak use and all types of users, including those with mobility restrictions.

- Corridors and circulation areas must comply with Fire Safety requirements (see Education (School Premises) Regulations 1999, DCSF Constructional Standards and current Building Regulations).

- Corridors shall be of an appropriate width to support the activities they serve and main circulation routes shall not be less than 1.8m.  Narrower widths depending on circumstances and traffic flow may be acceptable to access individual rooms.

- A minimum floor to ceiling height of 2.3m is required in new accommodation areas, though additional volume shall be exploited in appropriate places. Lower heights may acceptable in certain locations (such as entrance lobbies) but must be agreed with the client.

- As far as possible, long narrow corridors shall be avoided.

    - The Contractors shall be able to demonstrate, using specialist advice and computer modelling as necessary, how the width and position of stairs and internal circulation routes are safe and comfortable for all users at lesson changes and fire escape drills.

## External Space: Grounds

    - All external spaces should be well-designed and offer a variety of different settings for leisure, learning and sport should provide for formal and informal teaching and learning, as well as social and recreational, needs of the school community.

    - All designs shall address the following points as listed in the CABE review requirements for school grounds: making assets of the outdoor spaces:

- The grounds and planting should contribute to creating a sense of place

- The design should respond to the existing topography, climate and ecology of the site

- Outdoor spaces should be provided for a variety of different student social activities, interest ranges and group sizes

- There should be provisions for outdoor learning

- There should be opportunities for a wide range of physical activities

    - The Contractor should also be able to demonstrate how the designs for external spaces offer a variety of different settings for leisure, learning and sport and address the following further design and construction issues:

- Ensure that there are no leftover or unplanned outdoor spaces with little function or no access.

- All area accessible to pupils should be capable of being easily supervised and/or overlooked by internal spaces.

- Spaces between wings of buildings should be designed to avoid north-facing, sunless areas if they are to be used by pupils, and external social space should be in areas that are likely to be in the sun.

- The detailed design should pay attention to disabled access including provision of level thresholds.

### Typical Organisation

    - Requirements for the layout of the site, including the separation of access routes, are covered under Site Layout and Landscaping This section covers the requirements for the various elements of outdoor space, or school grounds.

    - Generally, all schools will comprise the following types of outdoor space, designed to accommodate a range of uses to suit the formal curriculum and the informal and social activities of pupils and to support curriculum delivery and community activities:

- outdoor classrooms forming an external learning area as part of the suites of spaces described above wherever possible;

- informal and social area, including soft grassed and/or landscaped areas and hard-surfaced recreational space [the area commonly known as ‘playground’], as well as habitat areas;

- hard-surfaced games area, marked out for games such as netball and tennis, in the form of a multi-use games area (MUGA) where ever possible;

- sports pitches, generally on grass or synthetic [turf] surfaces which shall include summer and winter games pitches and margins and overlapping or adjacent provision [on the same surface] such as cricket nets, running tracks and other athletic facilities;

- access areas, including paths, cycle routes, roads, delivery and bin storage areas, drop-off and parking.

    - There will commonly be some overlap in the use of these areas.  The layout of the site should allow for such overlaps, for instance, the use of hard surfaced games courts and the spaces around them for informal and social activities.

    - The design and layout of these areas should take account of the hierarchy of outdoor sports facilities identified by school in Part B2 of this Design Brief.

    - Some schools will also have supplementary site areas, as discussed [at 1.5.7] below. The Contractor’s proposals will be expected to provide the correct balance of these facilities, as described below and in the area data sheets for each school.

### Protection of School Playing Fields

    - The total area of the first four of the bullets above is the total ‘playing field’ area as defined in Section 77(7) of the School Standards and Framework Act 1998. Where the number of pupil places [the net capacity] is not changing significantly, the Contractor should ensure that this area is equals or exceeds the current amount available.

    - Schools that are not Academies or Pupil Referral Units but are new or where the number of pupil places [the net capacity] is significantly increasing, the total area of hard-surfaced games area and sports pitches, as described above, shall match or exceed the requirements for ‘team game playing fields’ in the Education (School Premises) Regulations 1999, unless agreed otherwise by the Local Framework User. In some cases, this will be achieved through the use of off-site playing fields or all-weather pitches, for which the area counts twice for purposes of the regulations.

### All-weather Pitches

    - Where specified, the construction and performance of artificial surfaces for sport, such as synthetic turf pitches, shall comply with the relevant British Standard. The choice of surface shall be based on performance, safety and durability, through:

- the properties best suited to the types of games to be played, such as the ‘ball bounce’;

- slip resistance and abrasiveness;

- wear resistance;

- maintenance requirements.

    - Where specified, floodlighting should be provided in accordance with paragraph 3.2.60.

### Informal and Social Areas

    - Informal and Social areas should cater for pupils according to their age and the layout shall accommodate various interests of pupils should by providing a variety of areas with different facilities and a mixture of hard and soft surfaces. Hard surfaces should be marked out with a variety of courts and games, preferably within a single enclosed area to assist with supervision.

    - Hard surfacing materials shall be varied and attractive and to standards relevant to the proposed use. Creative planting, varied in form and colour, should provide hardy, year round interest. It should address the need for shade during the summer months and for outdoor seating during break times.

    - Part of the hard-surfaced informal and social areas should be laid out for physical activities, such as playgrounds. These areas shall be flat and well drained, be safely away from windows and avoid physical barriers such as external fire escapes.

### Hard Surfaced Games Courts

    - Hard surfaced areas for games courts, and any adjacent or overlapping skills practice areas, should be provided to the area identified in the schedule of accommodation for each school. Surfaces shall comply with the evenness requirements of BS7044 part 4. They should be level, drain well and have an even surface, which is free of obstructions13.  Areas should be of a shape and size suitable to allow courts to be marked out, with reasonable margins, to the dimensions set out by Sport England

### Multi-use Games Areas (MUGAs)

    - Where several courts are provided, these should be combined wherever possible to provide a multi-use games area and these should be appropriate dimensions, in line with Sport England guidance, to suit a wide range of sports, including five-a-side football, basketball, hockey, netball, tennis (or short tennis) and volleyball14. At some schools there may be some sports which require a higher priority and this is reflected in the layout and specifications in Part B2 of this Design Brief.

### Sports Pitches

    - As well as responding to the specific requirements in the Part B2 of this Design Brief and the Area Data Sheets for outdoor PE and sport facilities in each school, the Contactor shall be aware of the recommendations in the Sport England design documents listed in the PfS BSF design guidance: PE & Sport, and BB85: School Grounds: A Guide to Good Practice, and should be able to show that the design of outdoor sport and PE facilities are in line with this guidance. In particular, where pitches are provided:

- pitch drainage and pitch construction should be provided in accordance with the recommendations in BB85;

- sports pitches on grass surfaces should be marked out for the curriculum needs which will vary according to season during the school year;

- there should be sufficient margins built into the design to allow for the pitch location to be moved annually to avoid wear;

- new pitches should be constructed to conform to green spaces document;

- sports pitches should be designed and constructed to a standard that allows the minimum specified use for both school and community, and economic to maintain.

### Pitch Layouts

    - For all mainstream secondary schools where the area of sports pitches is sufficient, the area should provide winter pitches for team games chosen by the school, such as soccer, rugby, hockey.  Allowance should be made for cricket pitches and a 400m running track to be laid out in the summer term.  The location of any cricket squares and running track should avoid the most heavily used areas of the winter pitches, such as goal-mouths.  Cricket squares may be fenced in winter to protect surfaces, as long as the other pitches can be accommodated around them.

    - The Contractor shall give careful attention to the layout of pitches, courts and practice areas and the proposals shall be agreed by the Framework User .  Their location, size and shape should be based on a number of considerations, including the:

- statutory requirements for sports pitches9

- safety considerations, including pitch margins and the direction of play (for example for cricket nets);

- gradient (a uniform fall of about 1:100 is ideal, but an even fall of up to 1:60 is allowable, or more if it is across the line of play)21;

- layout of winter games pitches and their relationships to summer athletics and cricket provision;

- orientation of pitches (a roughly north-south direction is generally desirable for most games)22;

- accessibility for maintenance equipment and water if irrigation is needed.

### Access Areas

    - Site design should take account of access needs of the Emergency Services and seek to resolve potential conflicts between different movements. Alternative surfaces to asphalt should be considered, where such access penetrates the site. All access roads must be of sufficient width and have geometry to give easy and safe access to all car parking access and delivery points without inconveniencing students, staff or visitors to the school.

### Paths, Roads and Delivery Areas

    - Pedestrian routes and cycle routes should be separated from vehicular access routes, as specified above.

    - Access and turning facilities should be provided to suit delivery vehicles, buses and cars for staff and visitors. Advice in respect of road widths, turning radii and adequacy of construction will need to be sought from the relevant Authority. Roadways should be arranged to eliminate reversing movements.

### Drop-off and bus turn around provision

    - A clear drop-off point should be provided close to each school entrance area for disabled pupils17.  Parental drop off and pick up point(s) will be specified on a school-specific basis. Works will need to be acceptable to Highways and Planning Authorities. The boarding and disembarkation of school buses shall be sited away from other traffic movements.

    - Any pick up/ drop off area shall be visible from highway to enable drivers to estimate whether there is space for them to enter. However, car parking and the pick up/drop off area shall not be the main feature of the vista of the site.

### Parking and cycle storage

    - Parking should be segregated where possible from other traffic movements. Parking space numbers are to be in accordance with current local and national policy and the agreed use of the buildings.

    - The parking area should be carefully positioned so that it does not dominate the main arrival area and entrance points round the building.

    - Cycle storage should be easily accessible to cyclists but overseen by buildings, ideally including the school office. It should be able to be accessed without crossing vehicular routes wherever possible.

Section 2: Design Outcomes

This section identifies the core design outcomes for the learning environment, including flexibility and adaptability, enhancing learning and ethos, and providing a secure and welcoming place for the community as well as pupils. It considers these requirements from ‘the inside out’ – from the activities to be accommodated in each suite of spaces to the broader implications of how the building and grounds reinforce the ethos of the school in the community.

## Flexibility and Adaptability

    - To suit changes in policy, technology  and changing demands of the curriculum and organisation, the building and grounds should be able to respond to changing school needs: with the flexibility to allow for short-term changes of layout and use, and adaptability for long-term expansion or contraction.

    - All designs shall address the following points as listed in the CABE review requirements for long life, loose fit: creating a school that can adapt and evolve in the future:

- The design should provide day-to-day flexibility for different types of learning and teaching

- The building should be adaptable to accommodate different organisational structures or pedagogies [over time]

- The design should allow for future expansion of the school

- A [wide] range of layouts should be able to be made using the proposed furniture

    - For educational reasons, each suite of spaces that includes basic teaching spaces shall be designed to be:

- adaptable to allow for future change, for instance through using standardised dimensions to the length and breadth of learning spaces, such that future change such as adaptations to the sizes of learning spaces can be relatively easy and economic;

- expandable within the building envelope to allow the area to expand into adjacent suites of spaces that may need less space, as well as into new buildings in the future.

### Flexibility

    - In conjunction with the responses to the F&E Brief and the ICT Output Specification, the Contractor shall provide a flexible learning environment wherever possible. In particular, this should be demonstrable in the general and light practical learning areas

    - Through the integration of movable furniture and equipment (see F&E Brief), the design of the buildings shall provide flexibility to allow for short-term changes of layout and use, [for instance through the use of sliding/folding walls.]

    - As discussed in the F&E Brief, all general and practical learning spaces shall provide a space that is sufficiently flexible to accommodate the broad range of activities identified in part B2 Section 2, by keeping any fixed furniture and equipment to the perimeter and leaving the centre clear for loose furniture.

    - Designers will be expected to show initial furniture and equipment layouts for key example teaching spaces. These can then be used to test the suitability of the building design proposal within the available space. It is essential to consider the particular activities taking place in each subject area, particularly for practical subjects such as design and technology, art, music and science, in order to refine the initial layout. [see F&E Brief]

### Adaptability

    - The secondary school of the future will have a wider range of learning spaces in a suite and is likely to need a different range of spaces [again] in the future, to suit the school’s developing organisation and pedagogy. Any learning space, other than large and performance or heavy practical ones, shall therefore be adjacent to other spaces wherever possible to allow them to be adapted in the future, as part of the suite. The configuration of spaces must be able to expand, contract and reform in as many ways as is economically feasible.

    - Contractors shall be able to demonstrate how a range of different sizes and types of spaces can be accommodated in these suites of spaces, with particular reference to the examples set out in Part B2 of this Design Brief. Each of these options require all but the smallest spaces to:

- be accessed directly from an adjacent circulation area;

- be an appropriate shape as well as size, demonstrated to suit a variety of furniture layouts (see F&E Brief); and

- have sufficient ventilation and daylight.

    - This is an area where a fully coordinated design approach between architect, structural engineer, services engineer and client is essential to ensure all the systems interact satisfactorily. The Contractor shall be able to show how the changes made use the design of the building, structure and services to ensure that all configurations can easily and economically allow:

- The partitions most likely to change, for instance those perpendicular to the external wall, to be easily demountable [by an appropriate building contractor];

- columns in the middle of any spaces are avoided;

- lighting systems are suitable with minimal change to switching circuits and luminaire positions (see Lighting);

- heating and other services are suitable with minimal change;

- fenestration, and any ventilation chimneys or ducts proposed, suit the need for natural daylight and ventilation and the repositioning of partition walls (for instance against mullions);

- acoustic standards, including through screeds, are suitable in any separate rooms;

- internal doorsets are suitable with minimal change (see internal doors);

- floor and other finishes are suitable with minimal work.

    - Within any adaptable suite of spaces, Contractors are encouraged to allow part of the primary circulation area proposed to be able to be used for other activities, for instance as part of an open area, over the life of the building. Contractors shall ensure that any such options are likely to be economically viable in the future and that they are designed to standards that will suit a potential learning space, including daylighting and ventilation.

### Expandability

    - Contractor shall be able to demonstrate how and where:

- A typical suite of spaces could be enlarged into an adjacent suite that could be smaller;

- the buildings would be able to be enlarged overall to provide further accommodation, as indicated in Part B2.

## 2.2	Enhancing Learning

    - The building should enhance the activities of teaching and learning through being a high-quality and aesthetically pleasing environment that will stimulate and inspire young people.

    - All designs shall address the following points as listed in the CABE review requirements for successful synthesis: making a design that works in the round:

- The design as a whole should offer a thoughtful, coherent and convincing response to the key issues of this site and brief

- The whole design should add up to more than a sum of its parts

- It should be a pleasure to work, eat, learn, play, teach and socialise in the school

- The school [design should have the potential] to be a cherished part of its locality

- The architectural approach should successfully meet the aspirations of the client and community

- The school’s design should help to deliver educational transformation

    - At its broadest level, enhancing learning is at the heart of both the Educational and Design Briefs, and will be the overarching justification for many of the requirements of the Design Brief.

    - The school has modelled the requirements of its proposed curriculum, inclusion strategy and pastoral organisation. Secondary schools will have used this to produce a curriculum analysis, for both the short-term and longer-term, which will have been used to inform and test the Schedule of Accommodation.

    - Within each learning space, or suite of spaces, the school will have identified the specific activities, or learning settings, that will need to be accommodated through the F&E (see F&E Brief) and specialist facilities inherent in the building, and these are set out in the Area Data Sheets.

    - In the Educational Brief, they will have considered the ways in which pupils will use these learning settings within some specific suites of spaces, and crucially how they will move from one to another within a typical learning session, lesson or longer project. The Contractor shall be able to demonstrate how these learning settings can be achieved in the relevant suites of spaces, and how easily and quickly the learning environment can be changed to accommodate a different set.

    - The Contractor shall ensure that the design shall not be such that it dictates a particular approach to teaching and learning or organisational arrangements, without the option for change, but shall instead allow the school’s own ideas to be realised and implemented.

## Enhancing school ethos

    - The building and its grounds should embody the schools’ vision and ethos, lift the spirits and raise aspirations.

    - All designs shall address the following points as listed in the CABE review requirements for identity and context: making a school the students and community can be proud of:

- The educational vision [, ethos and identity] should be successfully manifested in the design

- The design should strengthen the image of education locally

    - All new and refurbished buildings shall be designed to reflect individual school aims and to give the strong message of high expectation from the school and its other users. Designs should positively influence the behaviour and enthusiasm of pupils and staff.

    - The Contractor shall be able to demonstrate aspects of the design of the buildings and grounds that enhance and contribute to:

- the school’s ethos, as defined in the School’s SfC and Part B2 of this Design Brief, including any specific requirements identified;

- an humane, attractive and comfortable learning environment;

- reducing poor behaviour and stimulating positive behaviour;

- encouraging older pupils to stay on to further education;

- attracting community and business use;

- encouraging adults returning to education;

- attracting and retaining staff.

## 2.4	Identity and community context

    - The building should enhance and uplift its neighbourhood, with a layout that encourages broad community access and use out of hours, where appropriate. The design and use of the site should promote a public perception of a civic building, engender local ownership and consider the requirements of the wider community, including any conservation areas.

    - All designs shall address the following points as listed in the CABE review requirements for identity and context: making a school the students and community can be proud of:

- The school [design] should be inviting to the local community

- The design should respond and contribute positively to its locality

- The scheme should establish an appropriate civic presence for the school in the neighbourhood

    - Bidders should be able to identify how the building provides a strong identity to the school within the community.

    - The design of the building and grounds shall provide for potential use by the local community outside the core school day by providing:

- easy access from the pedestrian entrances, cycle storage and car parking areas to the entrances to be used by the community, using signage and lighting as appropriate;

- a clear and welcoming entrance for use by the community outside the day, with a [potential] reception area and easy access to facilities such as changing rooms, sports hall and main hall;

- facilities and equipment suitable for community use, including an accessible toilet within the area available to the community;

- equipment storage and lockers solely for community use, as required in the Schedule of Accommodation;

- simple ways of ‘locking off’ areas of the school not available to the community and a heating [and security] system which is zoned to allow the areas for community use to be heated while the rest of the school is unoccupied [see heating systems 3.2].

- easily accessible and well-lit outdoor facilities, as specified in Part B2 of the Design Brief.

## 2.5	Welcome and Secure

    - The buildings and grounds should be welcoming to both the school and the community while providing adequate security for pupils and staff and a feeling of a secure and environment that is a pleasure to use.

    - All designs shall address the following points as listed in the CABE review requirements for feeling safe: creating a secure and welcoming place:

- External routes and boundaries should be clear and well defined

- The security strategy should be balanced with openness

- There should be opportunities for passive surveillance at key points in the school

- The design of toilets, staircases and circulation areas should allow for visibility so that pupils can feel safe

    - The buildings and grounds shall be designed to be welcoming to both the school and the community, while providing adequate security and a feeling of a secure environment. Unless the Contractor can show that circumstances preclude it, and the Framework User agrees, the landscape design shall:

- have clearly defined boundaries

- provide no more than two easily controlled access points to the site where possible, located so that they are visible from public areas;

- avoid overly complex external building envelope forms which may create areas which cannot be easily supervised;

- provide obvious, well lit and visible pathways and access routes with clear lines of sight;

- avoid pedestrian routes surrounded by high vegetation or outbuildings;

- aim to keep vehicular movement within the grounds to a minimum and ensure car parks are open and visible with bays close to main entrances;

- locate informal and social areas, bicycle compounds, hard play areas and car parking such that they are overlooked from school buildings, to facilitate supervision

- ensure any landscaping shall not provide cover for potential intruders and shall not include loose materials that can be used for vandalism.

- And the building design shall:

- locate toilets in areas where they can easily be supervised (see Toilets);

- provide refuges for the protection of disabled people if they cannot be immediately evacuated from the building in case of an emergency;

- provide fire and emergency escape routes and access for emergency vehicles;

- provide secure compounds away from buildings for waste materials and recycling facilities;

- providing well organised internal circulation routes with good visibility for supervision (see circulation);

- provide good sight lines between internal and external areas to allow some  safe monitoring of visitor and pupil movement.

- ensure physical barriers do not obstruct views towards or away from school buildings and grounds.

    - Around the building perimeter, security shall be enhanced by:

- careful positioning of drainpipes and canopies that may otherwise provide unwanted access to high level windows and rooflights;

- avoiding building in recessed doors and alcoves that offer refuge;

- using sloped rather than flat roofs to make access more difficult;

- good lighting of facades and the use of security cameras where appropriate and agreed by the Framework User;

- avoiding thick planting areas close to the building that could provide cover from security cameras and users inside the building;

- providing a perimeter walkway clear of furniture and obstructions; and

- appropriate grounds perimeter fencing (see Fencing).

### Security Technology and Alarms

    - Where security technology is used, it shall be discrete wherever possible with more visible methods restricted to selective and targeted areas. School users should be made to feel safe but not overwhelmed or encumbered by high profile security.

    - Where protective systems, including access control, intruder alarms and CCTV, are installed, they shall comply with the technical requirements set out in Section 3 (see 3.2.14 Protective Systems)

### Fencing

    - The contractor shall provide or upgrade fencing around the perimeter of the site in line with requirements identified in Part B2 of the Design Brief.

Section 3: Environmental Conditions

This section identifies the specific requirements for the acoustics, lighting, heating and ventilation, and building services in the learning environment. It considers these requirements in a similar order to other standard documents, such as the capital cost proforma – from substructure to finishes and fittings.

3.1 	INTERNAL Environment

    - The internal environment should provide comfortable environmental conditions throughout including creative and maximum use of natural light, suitable ventilation for different activities and an appropriate level of personal control.

    - All designs shall address the following points as listed in the CABE review requirements for interiors: creating excellent interior spaces for learning and teaching, and resources: deploying convincing environmental strategies:

- The acoustic requirements of different spaces should be achieved

- The optimum orientation for different types of spaces should be considered

- The design of the elevations should respond to different orientations

- The ventilation strategy should provide a comfortable environment in which to learn in all seasons

- Spaces should be naturally ventilated where possible [and appropriate]

- Key spaces should be [designed to be] daylit for most of the year

- There should be an imaginative use of daylight to create uplifting spaces

    - Additionally, the Contractor shall ensure that the design addresses the following points in ensuring that good environmental conditions are provided throughout, including optimum levels of natural light and ventilation for different activities:

- Teaching and circulation areas should make the most of opportunities for natural light to avoid an institutional character;

- Ensure that there is adequate, easily controlled ventilation which is not obstructed or hindered by mechanisms to control solar glare;

- Similarly, ensure there is sufficient temperature control measures, especially in spaces experiencing high heat gain;

- The acoustic performance of the building is informed by early design decisions as well as the proposed construction and should comply with the relevant Building Bulletins and Part E of the Building Regulations.

- Local control for ventilation, heating, glare and light levels is preferred to centralised control;

- Designs should co-ordinate mechanical and electrical services, including exposed conduits, alarm boxes, fire hydrants and emergency notices.

    - The design of the external envelope shall limit noise intrusion from traffic, pedestrians, nearby industry and weather related noise in order to comply with the requirements detailed in this section.

### Acoustics

    - The Contractor will be required to carry out post construction testing and submit other details in order to demonstrate compliance with the acoustic requirements.

    - As well as responding to the specific acoustic requirements in the Area Data Sheets for each school, the Contactor shall be aware of the design guidance available in the DCSF Building Bulletin BB93 ‘Acoustics in School Design’ and be able to demonstrate how their proposals have been designed by an Acoustic Consultant to meet the legislative requirements to meet the Building Regulations Part E and BB93. In particular:

- Sound insulation requirements of BB93 [Part E applies to sound insulation between dwellings but BB93 overrides all other requirements of this document in relation to Schools];

- Indoor ambient noise levels, sound insulation between rooms as set out in the Area Data Sheets and BB93 Section 1;

- Mid frequency reverberation times measured in seconds as set out in the Area Data Sheets and BB93 Section 1;

- Speech intelligibility in all open plan areas, which shall comply with Section 1.1.7 of BB93 unless alternative performance standards are proposed in accordance with BB93 and agreed with the Framework User.

- Designing specific teaching areas to suit pupils with Special educational needs and disabilities such as hearing impairments, where this has been highlighted in Part B2.

- Site and internal room layout, provision of noise attenuation barriers and choice of ventilation systems.

    - The contractor will complete set of calculations to indicate compliance with BB93. Testing and remediation will be carried out to prove compliance.

### Daylight

    - Proposals shall demonstrate that natural lighting will be harnessed and controlled to best practice in terms of effective illumination, form, colour rendering, shading, glare and heat gains and losses.

    - Room dimensions, window dimensions, and surface reflectances shall be considered with the aim of reducing glare and maximising daylight uniformity.

    - The prime means of lighting shall be daylight in all occupied spaces. The Contractor shall therefore be able to demonstrate average daylight factors of at least x 2%using the BRE average daylight simulation software, unless specific site considerations make this unachievable, in which case the issues will be identified and agreed with the Framework User. In any case, the contractor shall clearly demonstrate the designed performance levels.

    - Surface reflectances and the disposition of glazing should be such that inter-reflected light in the space is strong and widespread.

    - The Contractor shall ensure that the uniformity of daylight conforms with EN15193 such that both (not either one) of the following conditions are satisfied:

- a significant part of the working plane (normally more than 80%) lies within the ‘no-sky line’]; and

- in a room lit by windows in one wall only, the depth of the room is not too large in comparison with the height and the width of the windows, as defined below.

    - In a room with windows in one wall only, the following inequality shall be satisfied, where

L/W + L/H < 2/(1-Rb)

L is the depth of the room from window to back wall, in metres (m);

W is the width of the room, measured parallel to the window, in metres (m);

H is the height of the window head above floor level, in metres (m);

Rb is the area-weighted average reflectance of the interior surfaces (walls, floor and ceiling) in the half of the room remote from the window.

    - The Contractor shall be aware of any design guidance available from the Society of Light and Lighting and be able to demonstrate how their proposals meet the best practice set out in Lighting Guide 5, BB90, EN12464 and CIBSE and CIE recommended guidelines. In particular:

- prediction techniques for solar gain;

- the calculation of the glare index.

    - As required under Sustainable Design, daylighting shall be designed to be maximised and to be integrated with the artificial lighting to take advantage of energy saving measures such as automatic daylight level sensors where possible.

Glare

    - The Contractor shall demonstrate a strategy to minimise glare. Readily adjustable and robust blinds are an important part of that strategy to allow the use of white screens and projectors, and to ensure that the teacher or speaker need not face glare or be seen against glare.

### Temperature

    - The Contractor shall be able to demonstrate how all parts of the buildings will comply with the minimum and, crucially, the maximum temperature requirements set out on the Area Data Sheets.

    - The Contractor shall be aware of [any design guidance available on temperature] and be able to demonstrate how their proposals meet the mandatory requirements set out in Approved Document ADL 2006, the Education (School Premises) Regulations 1999, BB87 and Building Regulations Approved Document L. In particular:

- building logs and energy performance certificates;

- Heating and ventilation systems shall be designed to be efficient as described in the current ADL 2006 i.e. at least 80.8% Seasonal Efficiency of gas fired boiler plant and Specific Fan Powers of 2W/l/s for fresh air ventilation or 0.2W/l/s for fan coils or recirculation;

    - The Contractor shall engineer the building to avoid wide thermal variations where possible and consider and integrate the selection and location of equipment, for example by choosing flat screen monitors for ICT suites that produce substantially less heat in learning areas.

### Solar Gain

    - The Contractor must provide peak solar gain temperature analyses in accordance with CIBSE prediction techniques where areas are exposed to direct sunlight to demonstrate acceptable solar gain against ambient air temperature.

    - The accommodation shall comply with the Health and Safety (Miscellaneous Amendments) Regulations 2002, to ensure that "excessive effects of sunlight on temperature shall be avoided."

    - The Service Provider shall also take specific note of the guidance relating to summertime overheating requirements in the DCSF Building Bulletins BB87 and BB101 and Building Regulations Approved Document L.

### Thermal Performance

    - The building fabric shall comply with the current Building Regulations Approved Document L2.

### Ventilation

    - The Contractor shall propose ventilation systems which has been carefully designed and considered to ensure that the ventilation specified in the Area Data Sheets is achieved and:

- all ventilation systems shall be capable of dealing with localised conditions and responding swiftly to changes in demand.

- All methods of ventilation shall be integrated into the building whether natural, passive or mechanical and co-ordinated with the fire alarm where required

- The systems shall be flexible to allow reduced ventilation rates with low occupancy or out of normal hour’s use

- Any discharge air terminals are positioned to prevent re-circulation into the building.

- Any trickle ventilation used shall be closable.

- Toilets and changing areas shall be ventilated at the minimum rate of 6 air changes per hour with appropriate time and occupancy controls.

    - The Contractor’s design proposals shall comply with the requirements set out in DCSF Building Bulletin 101, Building Regulations Part F and the Workplace Regulations.

    - Where kitchens or workshops require mechanical ventilation, the air change rates will be dictated by the CIBSE codes, and if necessary filtered make-up air shall be provided.

    - Should the Contractor’s ventilation strategy conflict with the requirements for acoustic performance it shall be identified within the proposals and clearly state the reason for and level of non-performance.

    - The efficient use of energy and heat recovery along with any other methods must be used with electrically operated ventilation systems.  The building design must reduce heat gains wherever possible hence reducing the need for mechanical ventilation or cooling, to offset high room temperatures.

    - Air infiltration in new premises (and premises that have received major refurbishment) shall be proven to be less than 8m3/h/m2 of façade area @ 50 Pascals, or any lower figure that may be required by the Building Regulations.

### Specialist ventilation

    - Additional ventilation measures will be required in certain areas as identified in the Area Data Sheets and in accordance with the Building Regulations Approved Document Part L2 , such as fume cupboards in science laboratories for the removal of noxious fumes, or local exhaust ventilation in rooms with equipment that increases the process load.

### Environmental Controls

    - Users shall have control over their immediate environment in terms of both heating and ventilation. All user controls shall therefore be easily comprehensible, accessible and quietly responsive. All controls should be located so as to deter use by pupils.

    - Controls must suit the operational requirements of the schools and should be accessible to users both physically and with regard to ease of use.

    - Specific controls may be required to be located to allow use by authorised personnel only. Where such requirements exist they shall be identified within Area Data Sheets. However, all controls should be located so as to deter unauthorised use by pupils.

## 3.2 	Building Services

    - The building should include suitable artificial lighting that enhances all learning environments but is complementary or supplementary to natural lighting, as well as appropriate mechanical and electrical installations.

    - All designs shall address the following points as listed in the CABE review requirements for resources: deploying convincing environmental strategies:

- The whole design should help to minimise energy use and carbon emissions

- Any on site energy generation should be appropriate and meaningful

- The design should provide an environment with a comfortable temperature for learning throughout the year

    - All designs shall address the following points in providing an integrated and responsive system of mechanical, electrical, protective and communication installations:

- All installations comply with all relevant Standards and Regulations in the design of building services for schools.

- Schools shall be capable of being metered separately for all utility consumption and for end use where required e.g. electricity used for lighting.

- Maximum internal noise levels due to plant and equipment shall comply with the requirements of Building Bulletin 93.

- Wherever possible, services shall be located and routed in order to maximise flexibility and choice for room layout (see Adaptability).

- Pipework, cables and equipment, where necessary, shall be easily accessible for maintenance but, wherever possible, hidden from view and made tamper-proof.

- All connections, distribution systems, components and containment systems shall be safely protected, tamper-proof, correctly insulated, free from exposed contacts and clearly labelled.

- All visible pipework and cable containment finishes shall be uniform in appearance, complete, clean and hygienic.

- All equipment controls and switchgear shall be permanently identified with appropriate warning notices and safety posters visible, firmly fixed and tamper proof.

- All plant, machinery and switchgear shall be guarded and locked where appropriate.

- Locks and interlocks shall be fitted as required by the requirements of the appropriate statutory bodies.

- The integrity of fire breaks within ceiling and roof voids shall not be breached by the installation of services.

### Heating systems

    - The heating system proposed shall be capable of providing the required temperatures to all locations in accordance with the requirements of the Area Data Sheets and the relevant statutory codes or codes of practice.

    - The heating medium, whilst consuming the minimum of prime energy, shall provide good comfort levels in all spaces through innovative design, and simple to operate controls, which harmonise with the user needs and the ventilation provision.

    - The Contractor shall ensure that design and installation of the heating systems shall:

- be robust and durable;

- include backup and standby facilities to ensure that the schools can function when minor failures of the system occur;

- be flexible enough to provide multi-functional use including third party use of the buildings without loss of energy efficiency and the use of complex control and operating systems;

- ensure that routing of heating pipes shall be co-ordinated with the building appearance and be routed such that major disruption to the schools is avoided as a result of minor repairs or routine maintenance;

- ensure that piped water services shall avoid rooms or areas where leaks would cause considerable disruption and financial loss;

- be designed to ensure that temperature variations are confined to those specified as acceptable in the Area Data Sheets;

- provide heating equipment capable of being controlled to deliver the required temperature to suit the range of activities identified for flexible and multi-purpose areas.

- ensure surface temperatures of heat and emitters and associated pipework are safe and in accordance with current Building Regulations and Building Bulletins

- include valve isolation such that isolation of circuits/ sub-circuits does not disrupt heating to the remaining building;

- include frost and anti-condensation protection.

    - The Contractor shall provide zoned systems matched to occupancy areas. These zones must have variable temperature controls and permit extra-curricular activity Individual thermostatic control must be provided to each room or space.

    - Ceiling mounted radiant panels will not be acceptable in classrooms or offices (unless demonstrated not to create uncomfortable conditions for seated occupants).

    - If boilers are used as the source of heating then the design shall ensure that the total standing losses of the boilers and heating distribution do not exceed 15% of the annual heating energy during occupied hours.

    - All submitted plans shall comply fully with the latest building regulations in force, in particular Part L2A (ADL 2006). The Contractor shall also be aware and comply with any future legislation, which may come into effect during the works, such as a requirement for energy certification under the European Energy Performance of a Building (EPBD).

### Heating controls

    - Space heating controls must be easy to use by untrained school staff, reliable and as far as possible automatic.  Adjustable components (thermostats) must be tamper-proof as required by the current ADL.

    - Specific controls may be required to be located to allow use by authorised personnel only. Where such requirements exist they shall be identified within Area Data Sheets. However, all controls should be located so as to deter use by pupils.

    - Control systems shall be provided with the facility for remote monitoring of the system.

    - For buildings greater than 1000m2 a BEMS or controls of similar sophistication must be installed, to include automatic meter reading, optimisation, weather compensation, scheduling, time extension, frost protection and holiday setting with a simple user interface.

### Water

    - Adequate outlets for the wholesome supply of fresh palatable drinking water shall be provided around the school, both internally and externally. Such outlets shall:

- be adequate for the number of pupil places

- be sited at a sufficient number of suitable locations for pupils throughout the school buildings, including within dining areas

- be positioned to be easily accessible by all pupils at all times, but physically separate from toilets and hand washing areas;

- have all drinking water supplies clearly and correctly marked as such.

    - Drinking fountains are required as a minimum in accordance with the following requirements:

- one number for each suite of spaces area per floor

- two number in sports reception area

- two number to main spine corridor per floor

- one number to sports pavilion

    - Care must be taken in locating these stations to avoid misuse, spillages and waste. The exact location of the drinking water supplies shall be agreed with the school and the Framework User.

    - Drinking water installations shall permit users to recharge water bottles using spigots and the supply system shall incorporate a ‘dead’ handle system to minimise spillages and prevent the water supply being left on. Drinking fountains must have appropriate drainage facilities and be sufficiently robust to deter casual vandalism.

    - The Contractor shall provide water service to outlet points:

- of the correct type, sufficient rate and suitable temperature to meet the prescribed standards and relevant Building Bulletins

- that supply mains or tanked cold water to external areas, for grounds maintenance, landscaping and fire fighting;

- that supply mains water or tanked potable water direct to internal areas, including kitchens, staff/rest rooms, technology rooms, vending machines and medical rooms, as detailed in the Area Data Sheets;

- designed to operate in a safe condition appropriate to the process, function and specific areas being served.

- That comply with BS6700 and BS6465 and are installed and commissioned in accordance with the provisions of the Health and Safety Commission Code of Practice for the Prevention and Control of Legionellosis and disinfected to comply with current standards.

    - The Contractor must provide suitable systems of water storage and hot water production that comply with the relevant Building Bulletins and complement the physical layout of the building and ensure energy efficient operation and meet the operation and requirements of the school.

    - The type and availability of supplies shall:

- be chosen to fit with the school requirements, considering such issues as storage availability, pressure and emergency provision.

- provide a final discharge temperature of hot water supplies in showers and taps used by pupils that shall not exceed 43°C.

- be metered by a device with the capability to be read electronically.

    - Where domestic hot water is supplied without local thermostatic control, all taps must be appropriately labelled and shall not be located in areas where pupils have unsupervised access.

    - Water supplies fed from storage tanks not designed for potable water provision shall be clearly labelled as “not drinking water”.

    - Water tanks, where required, shall have the minimum possible capacity to prevent stagnation and must be suitably located to allow for cleaning of the water tanks, and to comply with the regulations above.

    - The design of fossil fuel based hot water systems shall show a system efficiency of greater than 50% i.e. heat in the hot water at point of use must be greater than 50% of the fuel input.

    - Standing losses for electrically heated hot water services for hand washing must not exceed 10W/basin.

    - Water conservation measures shall be applied to minimise urinal water use, over pressure and taps left on.

### Drainage Installation

    - The Contractor shall ensure that drainage system provided shall:

- achieve hygienic conditions and the effective disposal of wastewater, surface water and all liquid waste from the school and its facilities’ activities.

- Be designed in accordance with appropriate codes of practices.

    - All drainage runs (including land drainage) to be clear of obstructions, set in line to the necessary falls and show no signs of pipe displacement.  All manholes shall be designed to receive the relevant imposed load, whether it is pedestrian or vehicular. All internal manholes shall be double sealed.

    - The Contractor shall ensure that:

- prior written agreement is obtained from the relevant authorities for discharge into the public system. Such written agreement shall include confirmation that the existing system has the capacity to accept the increased discharge, and should include the negotiation of any wayleaves required.

- all necessary detailed surveys, inspections and appraisals of all existing systems shall be carried out including the use of CCTV where required.

- adequate provision is made for the diversion, if necessary, of any existing below ground drainage or other services.

- the efficiency and sound condition of any existing drainage, to be utilised.

- the Environment Agency have agreed the planned methodology for surface water drainage.

    - Drainage to playing fields and all weather pitches will be designed and constructed in accordance with current guidance and in consultation with Sport for England

### Gas and Compressed Air Installation

    - Gas and compressed air installations and appliances must be provided where stated in the Area Data Sheets and installed in accordance with appropriate legislation regulations and guidance.

    - The gas isolation valve for each area of the building shall be situated within a securely locked area. If this is not possible, the valve handles shall have a security bracket and padlock fitted, or a proprietary system installed where the gas supply for each area is regulated through a key operated control panel utilising a solenoid valve.  All gas installations to be in accordance with relevant regulations and guidance.

    - Gas isolation and automatic proving/soundness testing shall be incorporated to laboratory and similar classroom areas. Gas supplies to kitchen equipment shall be interlocked with the mechanical ventilation system as appropriate. Gas detection equipment interlocked with safety shut-off valves shall be installed in internal boiler rooms. Gas installations shall be certified on completion to comply with all CORGI recommendations and statutory requirements.

    - Emergency shut off valves shall be provided as stated in the Area Data Sheets.

### Fire Fighting Installation

    - All fire fighting equipment shall be designed and installed in accordance with current guidelines, legislation and the fire officer’s recommendations, and certified as such.

    - All installations shall be in accordance with BB100.

### Sprinklers

    - Where sprinklers are provided, as agreed with the Framework User, they shall comply with the requirements set out in ‘SSLD Guidance Note 8: Roof Sprinklers in Schools’ such that any sprinkler systems shall be designed, installed to a recognised standard by specialist sprinkler contractors suitably qualified and experienced [i.e. certified to LPS 1048 and meeting Loss Prevention Certification Board approval], to ensure the effective performance of the system in the event of a fire and to satisfy insurers and/or approving authorities. They shall comply with the following standards:

- British/European Standard BS EN 12845: Fixed firefighting systems – automatic sprinkler systems – Design, installation and maintenance10.

- The LPC Sprinkler Rules, BS EN 12845 version11, in conjunction with Technical Bulletin TB 221, Sprinkler protection of schools12 and other relevant Technical Bulletins containing insurers’ requirements for sprinkler protection of schools.

    - All sprinkler systems are required to meet the relevant recommendations in BB 100 for property protection, so they shall be designed and installed in accordance with the recommendations of LPC Sprinkler Rules, principally BS EN 12845 and all applicable Technical Bulletins, with particular reference to TB 221.

    - Water supplies for sprinklers shall be as detailed in BS EN 12845, TB 221 and TB 22416. A fire brigade inlet should be provided for all stored water applications and sprinkler system water supplies shall be separate from hydrant supplies, hose reels and risers.

    - Additionally, where sprinkler installations are to be installed then:

- the Framework User shall require that the system is activated via temperature sensors which facilitate a localised response around the fire wall. This should ensure protection whilst reducing the risk of malicious misuse and also ensure the containment of water damage to the local site of the fire;

- the system shall comply with all requirements of the Insurance industry guidelines and any specifics of the Insurers for the building to allow the entitlement to sprinkler discount being applied to insurance premiums.

### Building Management System

    - In buildings greater than 1000m2, the Contractor shall provide:

- a centralised testing and monitoring of mechanical systems through a Building Management System;

- a graphic PC workstation to control the Building Management System;

- structured security access coding to prevent unauthorised access to the system.

    - The Contractor shall ensure that any Building Management System shall carry out the following functions, as and where appropriate:

- control and monitor space temperatures on a room-by-room basis;

- provide individual and automatic temperature monitoring and control for all occupied spaces on a room-by-room basis;

- provide optimum start, stop control of plant operation and weather compensation;

- permit time and holiday schedules and scheduled out-of-hours operation to be programmed;

- provide alarm and a hard copy record of any plant failure giving rise to a high or low temperature;

- log domestic hot water flow and return temperatures;

- monitor incoming gas, power and water consumption;

- provide a software based maintenance prompt system to assist planned maintenance;

- provide lighting controls; and

- monitor water tank storage temperatures.

### Internal Lighting [systems]

    - The use of natural lighting shall be maximized but enhanced in areas where light levels change abruptly to overcome shadows. This may be particularly relevant in areas such as changes of level in stairwells and above ramps to avoid shadow risers and clearly illuminate treads and surface changes. Windows and skylights in teaching areas and corridors shall also be positioned to avoid glare and excessive heat gain.

    - Lighting shall be designed to suit specific tasks or multi task areas.

    - Internal electric lighting shall comply with the requirements and recommendations in the ‘key performance requirements’ set out in ‘SSLD Guidance Note 4: Lighting Systems in Schools’, depending on the type of lighting specified for the room or space in the Area Data Sheets.

    - The Contractor shall be able to demonstrate that they have used an experienced lighting engineer in the design of the lighting systems, and will use an appropriate installation contractor, to ensure that the electric lighting design shall:

- enhance all learning environments, so that it appears attractive and interesting for all the people who use it: walls and ceilings shall be illuminated to contribute to these impressions;

- consider the colour appearance of the electric light;

- take account of how spaces may be used by the school, as described in Section 2, so that the lighting options available are sufficient flexible;

- mitigate against poor visibility of interactive whiteboards and computer screens;

- assume that natural daylight is the main light source in all learning environments, unless specified otherwise in the relevant Area Data Sheet, and that electric lighting should be complementary or supplementary to natural lighting;

- create imaginative lighting environments and avoids blandness or uniformity

- minimise glare [and flicker], for instance through the use of louvres on fluorescent luminaires and/or the use of indirect lighting solutions;

- provide sufficient contrast, colour rendering, direction and illuminance where necessary to satisfy the needs of pupils with visual and hearing impairments;

- only use lamps with an efficacy of 65 lumens/circuit Watt and avoids any incandescent lamps with low efficacy, such as tungsten, except in some exceptional circumstances for display lighting;

- only use efficient luminaires with a minimum light output ratio (LOR) of 80%;

- use high frequency control gear that avoids flicker and provides an efficient efficacy of the lamp circuit. Control gear for any fluorescent lamp should be either a type A (A1, A2, A3) or B (B1, B2) as defined by a CELMA11 energy class.

    - Illumination levels and luminaries must be in accordance with Building Bulletin 87 (latest edition), Building Bulletin 90, CIBSE Code for Lighting, Building Regulations Approved Document ADL2A and in accordance with the Area Data Sheets and prescribed standards.

### Efficacy

    - General lighting lamp efficacy shall be demonstrated to be greater than 65 luminaire lumens per circuit Watt. Electric lighting uniformity ratio shall be 0.8. In setting a lighting efficacy requirement care must be taken to distinguish lamp lumens/circuit Watt from luminaire lumens/circuit Watt or lamp lumens/Watt, all of which are used in the literature.

### Adaptability

    - In line with the requirements for flexibility and adaptability described in Section 2, the layout of lighting should allow for the easy repositioning of internal partition walls to create other spaces with each suite of spaces. Unless the Contractor can demonstrate a better solution, this will involve:

- luminaires are arranged perpendicular to the windows at standard centres, to match the structural dimensions chosen for partition wall positions, but are switched in rows away from the windows so as to be either dimmed or switched off during daytime, depending on daylight availability;

- a dedicated luminaire placed above the whiteboard to highlight the area where necessary [see F&E Brief], controlled locally with the facility for dimming;

- the diversity of luminaires is minimised wherever possible.

### Lighting Controls

    - With regard to lighting controls and switching:

- controls and switching shall well planned and suit both the operational requirements of the School and energy efficiency requirements (see sustainability);

- controls shall be clearly labelled and accessible to users both physically and with regard to ease of use;

- photocell and presence detection controls and systems shall be considered and balanced against the intended occupancy patterns and actual daylight calculations.

- manual over-ride facilities shall be provided to any automatic lighting controls.

    - There shall be careful control of lighting in spaces where the use of ICT is planned and with the use of projectors and interactive whiteboards becoming more extensive, lighting arrangements shall be adaptable.

    - Automatic daylight dimming is required in learning spaces, with separate control for each row of lights parallel with the window wall up to a room depth where daylight factors reduce to less than 1%.

    - Automatic absence detection or time controls shall be used to switch lights off in unoccupied rooms. Overrides will be time limited to turn back to default.

### Emergency Lighting

    - The Contractor shall provide functional and serviceable emergency lighting to ensure safe evacuation in an emergency and/or in the events of mains power failure, to be integrated with escape routes and doors, in:

- Escape routes, stairways and corridors without any windows;

- [Areas with dangerous machinery;]

- Areas accessible to the public during the evenings, including the main hall.

    - Emergency lighting shall comply with DCSF Building Bulletins 87 (latest edition),90 and 100 and BS 5266, BS EN 60598-2-22:1999, BS EN 50172, LG12, CIBSE and the Building Regulations Approved Document B, Fire Safety.

    - In areas used by the public during the hours of darkness, the emergency lighting shall be of the maintained type, meaning that the lamps contained in a luminaire will operate from the normal supply or from the emergency supply at all times.

### External and Specialist Lighting

    - The Contractor shall provide external lighting systems that:

- are designed in accordance with DCSF Building Bulletin 90, covering car parks, sports facilities, walkways and roads, entrances, particular building features and security requirements;

- incorporates lamps having an efficacy of at least 65 lumens per circuit watt fitted with both time controls and daylight level photocell controls

- achieve safe environments for people, traffic and the building;

- minimise light pollution and ensures light levels are kept within the limits as required by BS 5489 and avoid nuisance to the adjacent neighbourhood.

    - Specialist lighting shall be provided in areas where standard lighting is unsuitable, as well as in performance spaces requiring stage lighting systems, as specified in the relevant Area Data Sheet.

### Mains Distribution

    - Main switchboards, sectional switchboards and distribution boards shall be appropriate in terms of all electrical and mechanical criteria.  The switchgear shall provide for future extension affecting cabling and electrical loads up to a minimum of 20% above the base load for the completed school.

    - All switchboards and distribution boards shall be installed in secure locations and must be tamper and vandal proof.

    - All equipment shall be provided with durable labels, clearly marked with details of the equipment’s function and designation;

    - The Contractor shall provide a main switch panel for the incoming supply, and ensure that the panel shall:

- be of ‘form 4’ construction and consist of a main incoming Air Circuit Breaker (ACB), phase failure relays, full metering and Building Management System (BMS) connections for monitoring and Controls.

- have sufficient out going switch fuses / Moulded Case Circuit Breaker’s (MCCB’s) for submain distribution, lifts, Heating, Ventilation and Air Conditioning (HVAC) and fire alarm along with a minimum of 25% spare capacity.

- be fitted with an Automatic Power factor correction to bring the power factor as close to unity as practicable.

    - The Contractor shall provide local panel boards fitted with MCCB’s for larger loads that are remote from the main incoming panel. The Contractor shall ensure that the panels are fitted with sub metering and have a minimum of 25% spare capacity and shall have Building Management System connection for monitoring and control.

    - The Contractor shall provide power and lighting distribution boards to meet the local lighting and power needs, and ensure that the local distribution boards:

- have a minimum of 10% spare capacity to allow for future extension/expansion of the system

- are complete with main incoming switch/ isolator Miniature Circuit Breaker’s (MCB’s) and Residual Current Devices, and have a minimum of 25% spare capacity.

- are located in secure cupboards around the building that give ease of access for maintenance.

    - The Contractor shall ensure that the ICT-rich teaching rooms, large offices and in particular the communications centres shall have a separate distribution board for computer supplies.

    - The Contractor shall ensure that where separate boards are required that these shall have Uninterruptible Power Supply back up.

### Power Circuits

    - Power Circuit systems shall comply with the following requirements.

- The Contractor shall provide suitable RCBO / RCD protection against electric shock and circuit overload for all socket outlets.

- The power circuit system shall be designed to minimise interference to computers caused by electrical faults or failures. The Contractor shall provide the appropriate number and distribution of sockets detailed within the Area Data Sheets together with others required for general maintenance and other functions such as cleaning.

- The Contractor shall provide suitable protection against surges caused by both lightning and switching electromagnetic impulse to power circuits supplying ICT and other sensitive equipment.

- Sockets shall be located to support differing furniture layouts and methods of teaching and coordinated with room layouts and usage.

- Outlets for computer equipment shall comply with BS7671 section 607 (earthing arrangements for high leakage equipment).

- All sockets shall be sited safely away from potential dangers.

- Specific proposals for power circuits, such as the number of sockets in a room, emergency cut off switches or a 3-phase supply, shall be as detailed on the Area Data Sheets.

### Clock Installation

    - Clocks shall be provided by the Contractor in accordance with Area Data Sheets.

### Lightning Protection

    - All buildings shall be provided with suitable lightning protection systems in accordance with current codes. All lightning protection systems shall be tamper proof.

### Lift Installation

    - Lifts are not required to provide for general pupil and staff movement but for ensuring access is available to all areas by those with physical disabilities and assisting with the distribution of heavy furniture and equipment.

    - The lifts provided shall:

- be key protected, protecting use for disabled pupils, staff and visitors only;

- contain alarm communication devices such that school is aware of a trapped person; and communication can be made with a 24 hour help line via a direct link to notify an appropriate party of their location and initiate their release;

- Provide a lift capacity appropriate for the population.

    - Where lifts are required, the Contractor shall provide a lift traffic analysis identifying the speed of the lift, size and waiting time.  The minimum waiting time shall not be less than “good” as defined by CIBSE lift traffic analysis.

### Protective Systems

    - All Protective Systems, including Access Control equipment and cabling, shall be securely installed and be tamper- and vandal-proof from both the controlled and uncontrolled zones.

### Intruder Alarm

    - The Contractor shall provide the buildings with a comprehensive intruder alarm systems including access controls, which complement the building’s functions and operations and are enhanced as necessary in designated areas of high risk.

    - The alarm system shall:

- meet the requirements of BS4737 parts 1, 2 and 3, BS 6799 and NACOSS;

- Any utilise some form of monitored path to the alarm receiving centre, if a remotely signalling alarm;

- be capable of remote monitoring;

- be installed by an installer certified by an UKAS, (United Kingdom Accreditation Service) accredited certification body.

    - It is likely that any new systems will require confirmation technology before being granted Level 1 Police response. Further, any systems that lose Level 1 response due to the number of false alarm activations experienced will require the addition of confirmation technology before Level 1 is reinstated. (Confirmation technology means the ability to confirm that alarm activation is actually due to an intruder, through either internal CCTV pictures or microphone detected sound, both transmitted to the alarm receiving centre, or the sequential activation of detectors tracking an intruder’s progress through the premises).

    - As the benefit of detection is not just aimed at those breaking in to steal, but at any intruder who may just wish to cause damage, detectors shall be provided to cover all accessible perimeter areas.

### CCTV

    - CCTV shall be installed by the Contractor for the purposes of:

- monitoring of entrances; and

- building/site surveillance.

    - All CCTV systems shall comply with the requirements of EN50132-7 and be sympathetic to the adjacent land and neighbours and avoid intrusion into the private activities not associated with the school.

    - Systems provided for the reason in (a) above shall be capable of recording to a quality sufficient to afford the Framework User the capability to prosecute any persons committing unlawful acts.

    - The Contractor must provide systems designed specifically to be integrated into the architectural designs of the school, surrounding grounds and access control systems.

### Communication Systems

### Fire Alarm System

    - Fire Alarm systems shall be provided at the School and shall:

- comply to at least the standard of BS 5839 Type L1 or L2 as agreed with the Framework User;

- provide detection, alarm and identification

- be integrated with other reactive systems.

- provide visual fire alarm systems at appropriate locations.

    - The facilities shall comply with the following requirements for fire protection:

- Means of escape, fire-fighting equipment, automatic fire detection systems and fire signage provisions must all be agreed with the Fire Authority.

- The elements of the structure, finishes, fixtures and fittings must comply with all relevant legislation, guidance and codes of practice.

- Alarm detection and equipment shall be suitable for visually and hearing impaired users.

    - Half hour fire doors on corridors and stairwells, which are subject to heavy usage, shall have the facility to be held open by electro-magnetic contacts wired into the fire alarm system (see internal doors).

### Period Bell and PA Systems

    - Period bell systems shall provide tones/bells to denote the start of the daily School session and to identify the end of various periods. The systems offered shall be flexible enough to deal with changes to the timetable. Tones/bells employed shall be easily distinguishable from the tones/bells employed on the fire alarm system. The systems must have pre-set timings with manual override.

    - All systems shall cater for hearing impaired building users.

    - Audio systems shall be provided as detailed in the Area Data Sheets.

### ICT Infrastructure (data cabling and telecommunications)

    - The Contractor is required to provide a structured data cabling network to support the ICT systems that will be required within the school. This should integrate and link directly to the proposals for ICT managed service.

    - The data cabling network is likely to be used to support wireless connectivity, and may also be used for voice and CCTV communications.

    - The scope of the provision will include all ICT data and telecommunications equipment, cabling systems and containment, from connection to the statutory undertaker to connection point with the school equipment.  Systems and equipment will include:

- data system (including all hubs routers, switches and other similar devices but excluding servers) and all incoming service connections;

- server room end connectivity via patch panels mounted in acceptable server cabinets;

- telecommunications system;

- one payphone in the main entrance area;

- PABX equipment;

- Any other items defined in the ICT Interface Protocol, as being the Contractor’s responsibility, as detailed in Annex [5] of this document

    - The Contractor is required to provide telephone systems that use the same cabling as the computer network. All PABX will be capable of working with ‘Voice over IP’.  The telephone system shall be as specified in the Area Data Sheets and be capable of delivering the full range of functionality.

    - All wireless connection transponders shall be of intrinsically safe design and operate at “touch-safe” power levels at all times.

    - An Emergency Voice Communication system shall be provided at each fire refuge point (see 3.4.47 stairs and ramps). This enables occupants of each refuge to alert others that they are in need of assistance and to receive reassurance that this will be forthcoming.

    - ICT infrastructure should be designed and installed with due regard to the requirements of the ICT Output Specification and the ICT interface protocol included in Annex [1] of this document.

### TV Installation

    - The extent to which TV and satellite installations are required shall be detailed in the Area Data Sheets. Where specified, this should integrate and link directly to the proposals for ICT service and may be provide access to TV stations through other means.

    - Where required, the installations shall be capable of receiving and distributing digital transmissions and shall comply with all relevant British Standards.

## 3.3	Form and structure

    - The building should be well composed, with an efficient structure that allows future adaptability.

    - All designs shall address the following points as listed in the CABE review requirements for buildings: making form, massing and appearance work together:

- The building’s form and massing should be appropriate to the site

- The massing should create well proportioned internal and external space

### Substructure

    - The design shall ensure that the structure shall support all dead and imposed loadings from the superstructure, internal finishes, fittings and furnishings, services and building use.

    - The Contractor shall ensure that the design of the building structure complies with the following:

- The structural grid or layout will allow adaptability in all general and light practical areas.

- The structural design and choice of materials shall consider the potential impact on the ICT infrastructure and systems that are proposed, and may be used in future, including wireless technology.

- Design shall ensure that projections such as structural columns and piers in large spaces such as halls and circulation routes shall be limited. Where these are unavoidable appropriate measures shall be in place to ensure safety;

- Designing building structures and services to relevant Building Regulations, British Standards, Building Bulletins and CIBSE guidance in  accordance with the requirements of the contract;

- Structural elements of the internal and external areas are physically present and sufficiently sound to permit safe occupancy or use by the staff, pupils and other persons.

## 3.4	Building Fabric and Materials

    - The design should include a simple palette of robust, attractive, environmentally friendly materials and finishes, that are durable and attractive and will weather and wear well.

    - All designs shall address the following points as listed in the CABE review requirements for buildings: making form, massing and appearance work together:

- The elevations should reflect the design concept to create an inspiring building

- The materials should contribute positively to the quality of the scheme

    - The Contractor shall ensure that all aspects of the external building fabric and installations are designed to comply with the School Premises Regulations, the Constructional Standards of Section 4 of BB87 (latest edition) and the relevant sections of the Building Regulations, such that they provide resistance to penetration by rain, snow and wind and to moisture rising from the ground and minimise all disturbance from the elements in general.

### Use of Materials

    - All construction shall be carried out in accordance with the relevant current National Building Regulations and the appropriate British Standards Codes of  Practice for workmanship and materials

    - Without prejudice to the foregoing, the Contractor shall not specify in the design and use in the Works products and materials that are referred to as being hazardous to health and/or safety in “The Control of Substances Hazardous to Health Regulations” 2002 as amended or that do not comply with:

- The Montreal Protocol;

- The Construction Design and Management Regulations 1994 as amended;

- British Standards or equivalent European industry standards as amended;

- Codes of Practice; or

- Which are generally known within the European Union at the time of specification to be deleterious to the environment, health and/or safety or to the durability of other structures, finishes, plant and/or machinery.

- Asbestos or any products or materials containing asbestos;

- Substances that deplete the ozone layer as identified by the United Nations Development Programme.

    - Where cedar/timber cladding is specified the following conditions must be met:

- Cedar/timber cladding must be installed at a high level only;

- There shall be no overhanging eaves adjacent to cedar/timber cladding, to prevent the spread of fire;

- Cedar/timber cladding must be treated to Class O [and re-coated in accordance with the manufacturers recommendations for maintenance];

- Cedar/timber cladding must be on a non-combustible backing.

    - Materials shall be selected with due regard to their suitability, for purpose and performance, durability, ease of maintenance and repair, resistance to accidental or malicious damage and to their environmental impact. Minimal maintenance and ready and economical availability of replacement parts is also essential for the facility to operate smoothly and efficiently.

    - The Contractor shall use appropriate and robust materials and finishes that stand up well to the prevailing weather conditions, the ingress of ground and surface water and heavy use, whilst maintaining appearance over the long term. All areas of the building must be easily and safely accessible for cleaning and maintenance whilst preventing unauthorised access. It is imperative that the building is not aesthetically affected (even if only superficially) by the weather and the design must ensure no breakdown in the building’s fabric.

    - At Completion, the facilities are in such condition that they will achieve their anticipated life span as detailed below under the heading ‘design life. The planned maintenance programme required from the Contractor will use anticipated life span information to programme future maintenance and replacement regimes by a services provider.

### Roofs

    - The design and construction of roofs shall comply with the requirements set out in ‘SSLD Guidance Note 5: Roof Coverings in Schools’, such that the minimum standards set out in the ‘key performance requirements’, are achieved in all roofs wherever it is reasonable and appropriate. In addition:

- ETFE should not be used at low level, be easily accessible or used in situations where they are likely to be subject to malicious damage. Acoustics should be considered.

- In line with the CDM regulations (2007) requirement to ensure safety on roofs during the life of the building, HSE guidance shall be followed to: design out the need to gain access to the roof; provide glazing that can be cleaned from inside the building; provide guard railing or parapet to perimeter and stairs/door access or a travel restraint system.

    - Further to the requirements in the SSLD Guidance note, roof design and construction shall comply with the following requirements:

- Location of roof-lights shall be carefully considered to provide light to rooms below and sufficient security for School equipment.  Opening mechanisms for roof-lights must be carefully considered with controls such that pupils are discouraged from operating them.  Such openings shall also be robust and vandal-resistant from external entry by third parties.

- Overhanging eaves and canopies are not to be designed so as to provide an attractive sheltered area for miscreants, animals or birds. The fabric of the overhang shall be of non- combustible materials.

- Adequate fire barriers shall be present to ensure an externally set fire cannot enter the roof space through the eaves or elsewhere.

- The overall design of roof and surrounding elements shall not allow unauthorised access.

- The positioning and use of access hatches, inspection points, control gear, valves etc is such that it minimises disruption to the everyday running of the school.

    - Roof void ventilation shall be in accordance with relevant codes of practice.

    - Ventilators shall be installed in accordance with manufacturer’s instructions and in accordance with relevant codes of practice and British Standards at date of construction.

    - Thermal insulation in the roof void shall:

- not impede roof void ventilation

- be free from damage and breaks in continuity and integrity

- provide acoustic insulation and fire protection no less than that specified by current legislation.

### Chimneys and Flues

    - Chimneys and flues shall be designed to discharge all products of combustion to the chimney or flues point of termination without allowing any products of combustion to pass into any other areas.  Any chimney or flue shall also be designed to ensure that no water passes back down the chimney or flue through the incorporation of an appropriate termination fitting.

### Rainwater Goods

    - Guttering and rainwater pipework shall comply with the requirements set out in ‘SSLD Guidance Note 5: Roof Coverings in Schools’, such that the minimum standards for drainage set out in the ‘key performance requirements’ are achieved in all guttering and rainwater pipework wherever it is reasonable and appropriate.

    - Rainwater pipe detailing and arrangement shall be designed such that:

- it has uniform finishes and not show signs of oxidation on its external surfaces [at handover];

- it is robust enough to withstand accidental damage (for instance from ladders) during maintenance works, as well as vandalism;

- It incorporates measures to minimise build up of leaves, vegetation etc in the guttering;

- the use of internal down pipes is avoided, with all internal storm and foul drainage concealed;

- no water discharge is audible from within the building.

### Stairs and Ramps

    - The design and construction of all stairs shall comply with the requirements set out in ‘SSLD Guidance Note 6: Internal Stairways in Schools’, such that the minimum standards and dimensions set out in the ‘key performance requirements’ are achieved in all stairways wherever it is reasonable and appropriate.

    - Fire refuges shall be provided in each fire-protected stairway on each upper storey, as required by the Building Regulations Approved Document B: Fire Safety and shall be:

- located within the stair enclosure or in a protected space directly accessing the stair, for example, a lobby or compartment;

- a minimum of 1400x900mm and not reduce the width of the escape route;

- fitted with refuge signs and an Emergency Voice Communication system (see Communication systems).

    - The planning of stairway locations, design and size shall take into consideration:

- efficient and balanced use of stairs and other circulation provisions, such that [unless agreed by the Authoruty] fire escape stairs (especially enclosed cores) should not be redundant for normal usage;

- enhancing the adaptability of the spaces at the ends of corridors;

- [the effect of the staircase locations on potential for future expansion];

- The need for fire escape stairs should have a level exit directly to the outside of the building;

- reducing travel times between lessons, maximising time for learning and consequently promoting a calmer atmosphere;

- reducing congestion and maximising comfortable conditions through locating and sizing stairs appropriately.

- avoiding congestion by providing the greatest widths where pupil flows will be highest and avoiding single stairs and/or corridors in locations where it is likely that a majority of pupils will circulate class changeovers;

- allowing carry down evacuation for wheelchair users where necessary;

- promoting maximum views in from circulation routes and out to surrounding spaces to increase passive surveillance and the feeling of security.

- the option of placing doors on electro-magnetic hold-open devices linked to the fire alarm  and large glazed screens to circulation routes within the school;

- the option of grouping stairs, toilets and lockers together and locating staff workspaces nearby to maximise overlooking and student security from bullying (see Toilets).

- ensuring that stairs are easy to find and clearly differentiated for the benefit of new users and those with anxiety over familiar spaces (for example in autistic spectrum disorder.

### External Walls

    - External walls and materials chosen shall be designed and constructed to:

- be secure, robust, vandal-resistant and suitable for the particular circumstances and superimposed loadings;

- allow for the easy removal of graffiti;

- have finishes that conform to Class 0 as defined by Buildings Regulations;

- achieve U-value and performance requirements set by BB87 and the Building Regulations;

- have acoustic properties and performance in accordance with BB93;

- require maintenance that avoids disruption to the school;

- not allow unauthorised access to roofs or secure or restricted areas.

    - Non-combustible materials shall be used and, if high levels of insulation are required, Loss Prevention Certification Board (LPCB) products approved to LPS1181 Grade A shall be used. These shall have at least 30 minutes fire integrity and 20 minutes fire insulation.

    - External Insulated Finish Systems (EIFS) or similar cladding, which incorporates combustible materials shall not be permitted.

    - Consideration must be given to the insurance implications of using external timber cladding

### External Doors and Windows

    - External doors, windows and vents shall be designed and constructed to:

- have acoustic properties and performance in accordance with BB93;

- be positioned with regard to quality of light as well as ventilation regime.

    - Where significant areas of external glazing are exposed to direct sunlight, the Contractor must accommodate measures to reduce the affects of direct sunlight within their proposals in accordance with CIBSE prediction techniques and the references to solar gain and glare.

    - If external doors or windows are to be protected from intruders by security shutters, grilles or bars these must comply with BS8220 or have LPCB approval.

    - Windows and vents shall be designed and constructed to:

- provide sufficient light and natural ventilation (or supplement other ventilation to the required Part) in accordance with Building Regulations, DCSF Building Bulletins and statutory guidance;

- Be in line with Section D Item 2 Lighting and the requirements of the maximum use of natural light;

- be selected and positioned with due consideration to the acoustic requirements of this document and with regard to local acoustic conditions;

- in areas where ICT is used, have due consideration to establish appropriate lighting levels in order to prevent glare on screens, electronic whiteboards etc.

- be safe in closed or open positions and not be hazardous to persons passing by windows internally or externally when in use;

- prevent children from falling and / or climbing in / out at all levels;

- fitted with restrainers or similar devices as necessary;

- allow for the safe cleaning of windows;

- provide minimum maintenance to avoid future disruption to the School;

- not compromise the security of the building, with no internal beading.

    - Ironmongery and ventilator actuators or mechanisms shall be robust and tamper proof and must be easy to use/operate from floor level.

    - Window shading must be of a type that will not create a noise nuisance.

    - External doors shall be designed and constructed to:

- be robust enough to withstand heavy usage with minimal maintenance and to maintain the safety and security of the facility;

- take into account the different ages and abilities of all users;

- be vandal-resistant and incorporate appropriate controls and/or fittings to discourage misuse but afford safe operation and adequate security;

- allow disabled access, including access for motorised electric wheelchairs;

- ensure that door thresholds for wheelchair access are flush;

- Where appropriate draught lobbies are to be provided. These shall be configured so that single person passage at normal walking rate does not cause both doors to open at the same time.

    - External door ironmongery shall be designed to:

- allow for all doors including those to stores etc to be lockable with a suited key system or otherwise (eg card access) that shall be agreed with the Framework User;

- be robust and heavy duty

- provide letterboxes of a style and type (anti-arson) to be agreed with the Framework User;

- use door closers, where necessary, that take account of the age and needs of the pupils operating the doors.

### Internal Walls

    - The design and construction of internal partition walls shall comply with the requirements and recommendations set out in ‘SSLD Guidance Note 1: Partitions in Schools’, such that:

- The minimum standards set out in the ‘key performance requirements’, and defined in the Area Data Sheets, are achieved in all partition walls;

- the performance specifications, as set out in the five types of partition wall and the three types of partition finish, and defined in the Area Data Sheets, are achieved for the relevant type of partition wall and finish specified for the room or space in the Area Data Sheets. Where the wall is between two occupied spaces with different types required, the Contractor shall provide the higher of the two specifications.

    - In addition, all partition walls shall be designed and constructed to:

- be sufficiently robust to withstand impact damage from equipment and wheelchairs.

- be fit for their intended use and can suitably support finishes and fixtures where required.

- ensure that all walls and corners likely to be in contact with mobility and teaching equipment are adequately protected from damage to their finishes.

    - Finishes of all internal walls, and the internal face of external walls, shall:

- have smooth surfaces which have acoustic absorption qualities but are resistant to heavy use and are easy to maintain

- conform to the finish type (F1, F2 or F3: also based on the SSLD Guidance note) specified in the relevant Area Data Sheet.

### Internal Doors

    - Internal doors and frames shall comply with the requirements set out in ‘SSLD Guidance Note 7: Doorsets in Schools’ such that:

- The minimum standards set out in the ‘key performance requirements’, and defined in the Area Data Sheets, are achieved in all internal doorsets;

- the performance specifications, as set out in the seven types of doorset and the seven types of ironmongery set, and defined in the Area Data Sheets, are achieved for the relevant type of doorset and ironmongery specified for the room or space in the Area Data Sheets.

### Ironmongery

    - The design and installation of ironmongery to doorsets shall comply with the requirements set out in ‘SSLD Guidance Note 7: Internal Doorsets in Schools’ and:

- The Contractor must allow for all doors to rooms, stores etc., to be lockable with a suited key system or otherwise (such as card access) as agreed with the Framework User.

- The detail of the locking and suiting requirements to individual rooms must be agreed with the Framework User, and evidence must be given to the Framework User.

- All ironmongery shall be robust and heavy duty.

- Door closers shall take account of the age of the pupils operating the doors.

- Controlled (staff operated) emergency release required for toilet cubicle door locks

- Nameplates and numbers must be fitted to all rooms [as described in the Area data Sheets]. The detailed requirements to individual rooms must be agreed with the Framework User.

### Floor Finishes

    - The choice and installation of floor finishes shall comply with the requirements set out in ‘SSLD Guidance Note 2: Floor Finishes in Schools’ such that the minimum standards set out in the ‘key performance requirements’, and defined in the Area Data Sheets, are achieved in all internal areas of the buildings:

    - Suitable barrier matting shall be provided and maintained at external entrances to assist with cleanliness to internal floor coverings.

### Ceilings

    - Ceilings shall be designed, specified and installed to:

- have good light reflectance

- to be level and flush at joints, adequately secured and provide surface spread of flame performance in accordance with the relevant statutory codes;

- take into account and be sympathetic to the acoustic properties of each installation location;

- have acoustic properties and performance in accordance with BB93;

- ensure that they cannot be readily damaged by impact or be defaced;

- ensure any insulation used is non-combustible;

- be easy to maintain.

    - Moisture resistant ceilings will be required in areas such as kitchens, changing rooms, showers and toilets.

    - Ceilings within toilets and changing rooms shall be specified and designed such that they shall not be accessible by pupils. They must be robust, moisture proof and easy to clean.

### Decorations and Finishes

    - The Contractor shall provide wall and floor finishes as identified in the Area Data Sheets (see internal walls and floor [finishes]), which will include a consideration of their acoustics and noise reduction capabilities in line with the recommendations of BB93 ‘Acoustics in School Design’.

    - The Contractor shall be aware of the design guidance available in DCSF Building Bulletins and elsewhere on the suitability and effects of decorations and colour in school buildings, and shall be able to demonstrate that:

- variations of colour and texture provide a welcoming and stimulating environment;

- decorations and finishes fit with the school ethos.

## 3.5	Details and integration

    - The construction should be well thought through and detailed carefully to ensure an intelligent integration of building fabric, engineering and services, ICT infrastructure and furniture and equipment.

    - All designs shall address the following points as listed in the CABE review requirements for buildings: making form, massing and appearance work together:

- There should be a coherent design idea that relates plans, sections and elevations

- The building should be good architecture in its own right

### Fixtures and Fittings

    - [see F&E brief: Part C1 and 2]

### Sanitary Fittings

    - Sanitary fittings shall comply with the following requirements:

- Low-level cisterns to WCs concealed where possible and resist unauthorised access.

- WC seats to have strong fixing to pan. WC seats to be of a size appropriate to relevant user age group.

- Size and fixing height of sanitary ware must be appropriate for relevant user age groups and location (including taking into account the needs of disabled persons).

- No plugs required for wash hand basins in pupils’ toilets.

- Robust and tamper proof mixer taps with timed delivery.

    - Fixtures and fittings in the pupils’ toilet areas must be sufficiently robust to avoid vandalism.

    - Showers must be self-draining and allow privacy for users.

    - Where provided, urinals are to be individual to allow privacy for users.

### Signage

    - Providing signage throughout the schools and their surroundings will give clear indications of directions for all users but must be fully integrated into the design of the buildings and signs shall be of a uniform type and be positioned in a similar manner throughout. The final strategy for the level of signage, directional information and distinguishing features as well as the approach to general movement through the building must be agreed and approved with the school. The schemes devised may be highly individual depending on the schools’ size, pupil make up, and level of community involvement but must still conform to the relevant guidelines.

    - The facilities shall have appropriate signage to define their purpose. As well as satisfying the requirements for signage above and in Part B2 of this Design Brief, the Contractor shall provide signage:

- to every room or space, denoting the name or purpose and agreed numbering, and

- generally to denote suites of spaces such as faculties or departments

- for directional purposes to aid circulation within the buildings.

    - Signage shall:

- Be consistent and provided to support safe and efficient movement around the site

- Be capable of alteration where appropriate but not easily tampered with

- Be clearly visible, especially for visitors, directing them from the entry to the site to the visitor’s reception area, giving the visitor no excuse for wandering around the site

- Use appropriate size lettering with visual contrast to the background

- Be installed at an appropriate height.

    - The facilities shall have a main external school sign, detailing the name of the school and other pertinent information, which the Contractor shall provide in consultation with the school and the Framework User. The sign shall be illuminated and of a design that allows the incorporation of changes when necessary.

### Integration with ICT and F&E

    - [see F&E brief: Part C1 and 2]

    - Reference should be made to the ICT Infrastructure specification provided as part of this Output specification and to the separate ICT Services Specification. The Contractor will be expected to understand the full implications of these requirements on all other elements of the building and Services such as lighting, heating, furniture layout, security, maintenance, building materials etc. The Contractor shall ensure that they are incorporated as appropriate in order that they fully support and compliment the ICT requirements and at the same time fulfil the requirements associated with the design and performance of the individual element.

## 3.6	Sustainable design

    - A sustainable approach to design, construction and environmental servicing is required, to provide a resource-efficient school with low environmental impact, efficient use of energy and water and opportunities for recycling, both in the construction and operation of the building.

    - All designs shall address the following points as listed in the CABE review requirements for resources: deploying convincing environmental strategies:

- The whole design should help to minimise energy use and carbon emissions

- Any on site energy generation should be appropriate and meaningful

    - Many of the issues relating to sustainability require a multi-disciplinary approach and will be delivered by architects and engineers in close collaboration. Passive design and the exploitation of natural resources like daylight, ground temperature, night time air temperature, solar energy, rainfall, wind, etc is associated with form and fabric as well as M&E services. Links are therefore provided to other parts of this document which may treat these issues in more detail.

    - The Contractor shall be fully conversant with the following, and address all those issues that are relevant:

- Local Authority renewables contribution in their planning requirements, see Unitary Development Plans and Supplementary Planning Documents

- Local Authority's Waste Management Strategy

- LA21 objectives and targets: designs should take into account any plans developed locally and meet their targets and guidance.

- Environment Agency requirements for drainage/flood risk.

### Developing an Environmental Assessment

    - A BREEAM for Schools rating of not less than ‘Very Good’ shall be achieved for the completed project. The design shall comply with Building Bulletin 87.

    - Bidders shall submit a completed Pre-Assessment Estimator to be considered by the Framework User at the ITT evaluation stages.

### Water Conservation

    - 2.7 m3/person/annum is regarded as ‘Good Practice’ for schools (without pools) based on the Watermark project The Contractor shall describe their strategy, including the installation of water saving technologies, to meet this target.

### Low Carbon

    - Where more than 75% of the floor area of a school is new build, these shall be designed to have carbon dioxide emissions of 40% (60% less) of those of the 2002 standards. Compliance shall be demonstrated through completion of the DCSF Carbon Calculator.

    - This applies to new schools in Building Schools for the Future, One School Pathfinders and the Academies programme with at least a 75% new build element, and attracts a £50/m2 funding supplement. This is to be indexed from 1Q2007 but otherwise is all inclusive, i.e. it is considered to cover all design or additional fees and will not be supplemented by location factors.

    - The 60% target refers to the predicted energy use within school buildings that are currently being constructed compared to the energy efficiency standards set out in the 2002 Building Regulations plus emissions that can be attributed equipment such as computers and other appliances. Just to comply with current (2006) building regulations will entail considerable improvement over 2002 in any case.

### Energy Efficiency

    - Heating system controls should be designed to allow time and temperature overrides but they will default to automatic operation once a pre-determined time period has elapsed.

    - A large proportion of heat loss is due to the provision of fresh air for occupants which entails the rejection of energy laden warm or cool air. This can be reduced by the use of heat recovery. In any case a design for low infiltration will reduce the heat lost in draughts.

    - Passive measures, such as thermal mass and external shading, shall be exploited where possible to reduce the possibility of overheating. Consideration should be given to minimising heat load by the use of efficient equipment including ICT. Where, after consideration of such measures, heat load, acoustics, or air pollution is such that mechanical cooling is required, low carbon cooling systems will be considered in preference to conventional air conditioning.

    - An Energy Performance Certificate shall be provided on behalf of the Framework User. This is a duty under Building Regulations. Ventilation

    - Natural ventilation will be utilised in preference to mechanical cooling. The natural or mechanical ventilation strategy will comply with the requirements of BB 101 and meet the criteria for avoidance of summer overheating (see summertime overheating).

    - Occupants need to be able to control the ventilation system, regardless of the system used and will comply with the requirement of BB 101 with regards to the safe opening and closing of windows.

    - In order to assist the sizing of ventilation opening for natural ventilation design the ClassVent calculator tool has been published. The ClassVent calculator tool will demonstrate compliance with the required airflow performance standards.

    - BB101 states the minimum ventilation requirements for natural ventilation and mechanical ventilation. These need to be considered with the ventilation performance standards for avoidance of summertime overheating. Two of the following three criteria must be met to show the proposed school will not suffer overheating:

- There should be no more than 120 hours when the air temperature in the classroom rises above 28°C

- The average internal to external temperature difference should not exceed 5°C (i.e. the internal air temperature should be no more than 5°C above the external air temperature on average)

- The internal air temperature when the space is occupied should not exceed 32°C.

    - In order to assist in determining possible overheating in classrooms as indicated by these performance parameters, the ClassCool tool has been published by the DCSF. The ClassCool results are presented in terms of the above performance parameters and would demonstrate compliance with the performance standards.

    - Note that other appropriate tools for predicting the required parameters can be used and if so should use the geographically closest CIBSE Test Reference Year.

### Lighting Efficiency

    - Lighting efficiency shall be as required in this Design Brief in paragraphs on Lighting Efficacy, Lighting Controls (see Lighting systems) and daylighting (see Daylight)

    - This will mean making the maximum use of daylight, using electric light to complement daylight, and using energy efficient lighting that only operates when it is required.

    - Lighting controls will consider the positioning of the control switches, and the organisation of the lighting circuits is to relate to the daylight distribution and to the use of the space.

    - The type of luminaries will be chosen to give an efficacy of not less than 65 luminaire-lumens/circuit-Watt.

    - Lighting maintenance will be considered.

    - The daylighting criteria, maintained illuminance (Lux) levels, lighting quality, external lighting and emergency lighting will comply with the requirements of BB 87.

### Efficient Equipment

    - Equipment shall be procured with energy efficiency in mind. Domestic appliances shall be ‘A rated’. In consideration of ICT, energy efficiency will be considered alongside performance.  [see F&E Brief]

### Climate Change Adaptation

    - Contractors shall ensure that the design school site(s) is resilient to present and future climate through the use of the adaptation toolkits developed by the UK Climate Impacts Programme.

### Materials Efficiency and Reducing Waste During Construction

    - The project will support national policy goals (e.g. halving waste to landfill by 2012, adopted in England by the Government’s Strategy for Sustainable Construction), by reducing waste, recovering more materials and using more recovered material in new build.

    - To help achieve sustainable development, materials efficiency should be considered at every stage of the design and construction process. Guidance to assist designers and contractors to understand and meet these requirements and to improve performance in BSF projects is available from WRAP.

    - The use of the Net Waste Method and WRAP’s Net Waste Tool should be considered as it converts recycled content and waste into a common unit, namely value, which allows a trade-off between the two.

    - The Contractor is required to:

- implement a Site Waste Management Plan that not only meets the requirements of the Site Waste Management Plans Regulations 2008 but exceeds these requirements by setting project-specific targets for waste reduction and recovery and measuring performance,

- measure and report the quantity of waste produced (tonnes of waste per £100k of construction spend and per m2 of building area),

- measure and report the quantity of waste sent to landfill (tonnes of waste to landfill per £100k of construction spend and per m2 of building area),

- recover a minimum of 80% of construction and demolition materials.

    - The Contractor shall forecast wastage and set targets for waste reduction from the design stage (for instance by using WRAP’s Net Waste Tool ), and to monitor and report the forecast and actual performance.

### Requirement for higher recycled content

    - The Contractor will ensure that at least 10% of the total value of materials used in construction and refurbishment derives from recycled and reused content in the products and materials selected.  The Contractor must also demonstrate that the most significant cost-neutral opportunities to increase the value of materials deriving from recycled and re-used content (known as ‘Quick Wins’) have been identified and considered, that good practice has been implemented where technically and commercially viable, and that the targeted improvements made in the total recycled content above “baseline practice” for the project have been quantified.

    - WRAP’s Net Waste Tool is available on-line to demonstrate forecast recycled content and actual performance.

    - The Contractor is required to submit a final report summarising performance on waste materials to the Framework User upon completion of the building works, in a format to be agreed by both parties.

### Timber

    - Suppliers and contractors to Government should have available documentary evidence demonstrating the timber supplied is:

- at a minimum from legal sources, and

- if promised, from sustainable sources.

    - This evidence should include full chain of custody from the forest source(s) to the end user.

    - Bidders are given the option of offering sustainable timber as an addition to the minimum specification. This ‘variant specification’ includes all the minimum criteria as well as a requirement that a minimum of 70% of the material (by category) is from a sustainable forest source, which can be either recycled wood and/or virgin timber from an adequately managed forest source. More information is available from CPET (Central Point of Expertise on Procurement of Timber)

Section 4: Facilities Management and Construction

This section covers the design issues that have implications for durability, operability, maintenance and renewal of components, over the life of the buildings. It also covers the compliance with regulations and guidance and how the construction can be timed and phased with the least disruption to the school if it is on the same site.

## 4.1	Operability

    - The engineering systems and components of the building should be easy to operate, and the user should be able to easily adjust or operate components that affect their comfort, such as lighting switches and openable windows.

    - All designs shall address the following points as listed in the CABE review requirements for interiors: creating excellent spaces for learning and teaching:

- The building should work well in full use

## 4.2	Design Life and Maintenance

    - The building should be easily cleaned and maintained using materials and components that will have a suitable design life and can be easily and safely replaced when necessary. The choice of materials, services and components should ensure minimum inconvenience and disruption from breakdowns, repairs and maintenance activities.

    - All designs shall address the following points as listed in the CABE review requirements for buildings: making form, massing and appearance work together:

- The fabric of the buildings should be durable and easy to maintain

    - The service lifespan assessment shall be as defined in ISO 15686 Part 1 Buildings and Constructed Assets – Service Life Planning, General Principles.

    - The structural and non-replaceable components for buildings shall be specified as having a life of 60 years or more. Replaceable components shall have a life appropriate to the structure.

    - The principal elements of the building structure, external envelope and external civil engineering elements shall have a minimum life expectancy at Date for Completion as set out in the table below.

    - The design life of the building elements as a minimum shall be:

- Substructure – 60 years

- Frame, upper floors and stairs – 60 years

- Roof structure – 60 years

- Roof covering – 30 years

- External walls/cladding – 40 years

- Windows and external doors – 25 years

- Internal partitions – 25 years

- Internal finishes – 15 years

- Ceilings – 25 years

- Internal doors – 25 years

- Internal fixtures and fittings – 15 years

- Sanitary and catering facilities – 20 years

- Engineering Services (major components) – 25 years

- Lifts – 15 years

- Underground drainage – 60 years

- External finishes – 25 years

- External fences – 25 years

- External services – 25 years

- Site Works – 25 years.

### Planned Maintenance Programme

    - The Contractor shall provide a planned maintenance Programme for all elements requiring maintenance.

    - Where the Contractors proposals do not meet these minimum standards for service life, it shall be clearly identified by the inclusion of a table, within these proposals, similar to the above and listing the same building elements along with the required and proposed service lives. In addition, the contractors proposals shall include a clear and detailed statement of the reasoning behind this variation on the requirements, proposals for carrying out the additional maintenance and replacement works without disrupting any school (and third party) activities, details of any possible risks to the Framework User and school and third party activities associated with these proposals and any additional benefits that may be passed on to the Framework User or school as a result.

    - For any conversion and refurbishment works to existing buildings, or for buildings retained unaltered, the Contractor shall also clearly identify where these standards and service life criteria will not be achieved and provide the details as listed above.

    - Irrespective of the type of work to be undertaken, the Contractor shall provide full and clear proposals for programmes of planned maintenance and/or replacement that identify, but shall not be limited to, timescales, replacement intervals, scope of works etc. These proposals shall be detailed enough for the Framework User to assess the full impact on the delivery of all Services of any variation from this Specification.

    - The Contractor shall provide safety and security of access for internal and external maintenance purposes; including boarding, ladders and handrails within roof spaces.

    - The Contractor shall ensure that measures are incorporated to prevent birds roosting or nesting on the structure, especially around building entrances.

    - There must be no visible signs of entry to weather caused by a breakdown in the building fabric or its installations. There must be no discomfort to occupants as a result of weather penetration due to this cause.  Any water penetration will also be measured by electrical conductivity tests.

    - The design shall give regard to the practicality of maintenance, in particular:

- standard practical detailing in materials and using construction methods that are considered will be in use in the foreseeable future

- ease of access for maintenance.

### Maintenance Access

    - External maintenance access shall be designed and installed in accordance with current regulations and allow for all necessary access for cleaning and maintenance safely easily and without disruption to normal school operations.

    - Any walkways shall be compliant with all Health and Safety and manufacturers requirements. Walkways to roofs shall be adequately secured, free from corrosion, and decorated in accordance with the external decorations section.

### Finishes

    - The Contractor shall provide a selection of decoration and finishes that:

- is able to withstand heavy usage and potential vandalism;

- is resilient to impact and minimise noise;

- is easily cleaned and maintained.

    - Additionally, external finishes shall be:

- continuous in colour

- durable and resistant to weathering

- designed with materials that shall allow for the easy removal of graffiti.

4.3 	Compliance with Standards and Guidelines

    - The environment should meet all recommended standards and policies as listed in Annex [1 and 2] in addition to legislative and local requirements

    - All designs shall address the following points in complying with standards, guidance and guidelines:

- The building should be designed so that it can be safely constructed

- Removal or containment of hazardous materials should be managed safely

    - General design obligations on the Contractor include:

- Obtaining all statutory consents for the design and construction of the project including but not limited to: any necessary roads construction consents for any public roads and footpaths, including adoptions under Section 38 of the Highway Act 1980 or Section 104 of the Water Industries Act 1991 for highways and drainage;

- Designing facilities shall comply with Applicable Laws and Statutory Requirements;

- The Accommodation shall comply with the Area Data Sheets.

    - The Contractor shall comply with all relevant statutory and health and safety legislation and other industry standards, including British, European and International Standards. The Contractor shall also comply with the requirements of other National guidance including publications by the DCSF and other National Authorities where applicable.

    - Compliance with these regulations, standards and guidelines shall be taken as those being in force or published as at the date of Contract signature or foreseeable at the date of Contract signature.

    - All accommodation and facilities shall meet the standards where applicable in guidance published by the DCSF and other national bodies as indicated in the non-exhaustive list identified in Annex 1.

4.4 	phasing and Construction

    - The Contractor shall be able to demonstrate that the construction work shall be timed and phased to ensure:

- the least disruption to the school, particularly where they are on the same site.

- a reasonable time for the placement and installation of F&E and ICT

- occupation by the school at least two weeks before the start of a new term, leaving time to set up and move in to the new premises

- the location of any rooms or staff workstations are changed no more than three times.

    - The proposed timing of the landscaping shall ensure that sports pitches and hard surfaced games courts are available before, or as soon as possible after, occupation.

Department for Education and Skills (2007) Schools for the future: Inspirational design for kitchen and dining spaces. London; DFES Publications

The School Food Trust (2007) A fresh look at the school meal experience

If Bidders consider that it is not appropriate or they are not able to meet the requirements detailed here in respect of specific area(s) of a school, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

13 BS7044 part 4 gives detailed guidance on surface evenness and other aspects such as finished profile.

14 Refer to Sport England Technical Guidance Note 374 (Multi-Use Games Areas)

21 Refer to Handbook of Sports and Recreational Building Design Volume 1: Outdoor Sports, page 132.

22 Refer to Handbook of Sports and Recreational Building Design Volume 1: Outdoor Sports, page 170.

17 Refer to Building Bulletin 91: ‘Access for Disabled People to School Buildings’, DfEE 1999.

http://www.teachernet.gov.uk/docbank/index.cfm?id=5648

PrEN 15193: Energy performance of buildings — Energy requirements for lighting

If Bidders consider that it is not appropriate or they are not able to meet the requirements detailed here in respect of specific area(s) of a school, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

If Bidders consider that it is not appropriate or they are not able to meet the requirements detailed here in respect of specific area(s) of a school, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

If Bidders consider that it is not appropriate or they are not able to meet the requirements detailed here in respect of specific area(s) of a school, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

If Bidders consider that it is not appropriate or they are not able to meet the requirements detailed here in respect of specific area(s) of a school, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

If Bidders wish to propose a solution which they consider to be as good or better than that identified above, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

If Bidders consider that it is not appropriate or they are not able to meet the requirements detailed here in respect of specific area(s) of a school, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

If Bidders consider that it is not appropriate or they are not able to meet the requirements detailed here in respect of specific area(s) of a school, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

If Bidders consider that it is not appropriate or they are not able to meet the requirements detailed here in respect of specific area(s) of a school, please include a table setting out the following information:

- the relevant area(s) where is it proposed that a specific requirement should not apply;

- a clear cross reference to the requirement it is proposed should not apply to such areas; and

- an explanation as to why the Bidder considers it is not possible or appropriate for the particular requirement to apply to the relevant area(s).

http://www.ogcbuyingsolutions.gov.uk/energy/watermark/downloads/watermark_project_final_report.pdf

http://www.communities.gov.uk/publications/planningandbuilding/nondwelling

The following reference leads to BB101, ClassCool and ClassVent http://www.teachernet.gov.uk/management/resourcesfinanceandbuilding/schoolbuildings/environ/iaq/

http://www.ukcip.org.uk/

http://www.ukcip.org.uk/index.php?option=com_content&task=view&id=147&Itemid=273

www.wrap.org.uk/construction

http://nwtool.wrap.org.uk/

Following the method for construction waste measurement and reporting agreed by the UK Contractors Group

Freely accessible at http://nwtool.wrap.org.uk/

http://nwtool.wrap.org.uk/

http://www.proforest.net/cpet/uk-government-timber-procurement-policy/contractual-obligations